## bus name
Short Bus Code | Full Name | Long | Lat | Country | Full Name
AA | Ardnacrusha | -8.6029 | 52.7104 | Ireland | Ardnacrusha | substation
AD | Aghada | -8.209 | 51.837 | Ireland | Aghada | substation
ADM | Adamstown | -6.4539 | 53.3338 | Ireland | Adamstown | substation
AGH | Aghyoule | -7.5891 | 54.1721 | Ireland | Aghyoule | substation
AGL | Agannygal | -8.5499 | 53.0368 | Ireland | Agannygal | substation
AGN | Aungierstown | -6.4496 | 53.3144 | Ireland | Aungierstown | substation
AGI | Agivey Cluster | -6.5942 | 55.0462 | Ireland | Agivey Cluster | substation
AGT | Aught | -7.3055 | 53.7798 | Ireland | Aught | substation
AGY | Ardnagappary | -8.2894 | 55.0697 | Ireland | Ardnagappary | substation
AHA | Ahane | -9.1505 | 52.4671 | Ireland | Ahane | substation
AIR | Airport Road | -7.7798 | 52.0313 | Ireland | Airport Road | substation
ANR | Anner | -7.3055 | 53.7798 | Ireland | Anner | substation
ANT | Antrim | -6.2072 | 54.7195 | Ireland | Antrim | substation
ARI | Arigna | -8.1125 | 54.0763 | Ireland | Arigna | substation
ARK | Arklow | -6.1599 | 52.7977 | Ireland | Arklow | substation
ARM | Armagh | -6.6528 | 54.3503 | Ireland | Armagh | substation
ART | Artane | -6.1972 | 53.3825 | Ireland | Artane | substation
ARV | Arva | -7.5799 | 53.9214 | Ireland | Arva | substation
ATE | Athea | -9.2876 | 52.4606 | Ireland | Athea | substation
ATH | Athlone | -7.9407 | 53.4239 | Ireland | Athlone | substation
ATY | Athy | -6.9857 | 52.9918 | Ireland | Athy | substation
AUG | Aughinish | -9.0661 | 52.6211 | Ireland | Aughinish | substation
BAG | Barnageeragh | -6.1444 | 53.5834 | Ireland | Barnageeragh | substation
BAL | Baltrasna | -6.6804 | 53.5762 | Ireland | Baltrasna | substation
BAN (I) | Bandon | -8.7351 | 51.7459 | Ireland | Bandon | substation
BAN (N) | Banbridge | -6.2705 | 54.3487 | Ireland | Banbridge | substation
BAR | Barrymore | -8.2547 | 52.0959 | Ireland | Barrymore | substation
BCM | Ballycummin | -8.6634 | 52.6191 | Ireland | Ballycummin | substation
BCT | Bancroft | -6.3518 | 53.2933 | Ireland | Bancroft | substation
BDA | Baroda | -6.7833 | 53.1808 | Ireland | Baroda | substation
BDM | Ballydam | -7.3055 | 53.7798 | Ireland | Ballydam | substation
BDN | Ballydine | -7.5066 | 52.3644 | Ireland | Ballydine | substation
BDV | Barnadivane | -8.9675 | 51.8202 | Ireland | Barnadivane | substation
BEG | Ballybeg | -7.1422 | 52.2421 | Ireland | Ballybeg | substation
BFP | Belfast Power Station | -5.9301 | 54.5973 | Ireland | Belfast Power Station | substation
BGD | Belgard Road | -6.3768 | 53.3025 | Ireland | Belgard Road | substation
BGH | Boggeragh | -8.9167 | 52.0167 | Ireland | Boggeragh | substation
BGT | Ballyragget | -7.3329 | 52.7889 | Ireland | Ballyragget | substation
BIN | Binbane | -7.1227 | 54.0171 | Ireland | Binbane | substation
BK | Bellacorick | -9.5844 | 54.11 | Ireland | Bellacorick | substation
BKM | Bunkimalta | -8.2687 | 52.7417 | Ireland | Bunkimalta | substation
BKY | Barnakyle | -8.6999 | 52.6043 | Ireland | Barnakyle | substation
BLA | Blackrock | -6.1771 | 53.3008 | Ireland | Blackrock | substation
BLC | Belcamp | -6.1903 | 53.4081 | Ireland | Belcamp | substation
BLE | Ballinknockane | -10.085 | 52.2395 | Ireland | Ballinknockane | substation
BLI | Ballylickey | -9.4378 | 51.7215 | Ireland | Ballylickey | substation
BLK | Blake | -6.8812 | 53.2886 | Ireland | Blake | substation
BLU | Blundelstown | -6.5354 | 53.4461 | Ireland | Blundelstown | substation
BMA | Ballymena | -6.2802 | 54.8653 | Ireland | Ballymena | substation
BNH | Ballynahinch | -5.8974 | 54.4029 | Ireland | Ballynahinch | substation
BNM | Belfast North | -5.9301 | 54.5973 | Ireland | Belfast North | substation
BOG | Banoge | -6.2719 | 52.6468 | Ireland | Banoge | substation
BOL | Booltiagh | -9.2284 | 52.7811 | Ireland | Booltiagh | substation
BPS | Ballylumford Power Station | -5.7808 | 54.8456 | Ireland | Ballylumford Pow- er Station | substation
BRA | Bracklone | -7.1704 | 53.1507 | Ireland | Bracklone | substation
BRI | Brinny | -8.698 | 51.7873 | Ireland | Brinny | substation
BRO | Brockaghboy | -6.7382 | 54.9373 | Ireland | Brockaghboy | substation
BRT | Bracetown | -6.4594 | 53.4277 | Ireland | Bracetown | substation
BRY | Barnahely | -8.333 | 51.8285 | Ireland | Barnahely | substation
BUF | Buffy | -7.3055 | 53.7798 | Ireland | Buffy | substation
BUT | Butlerstown | -8.7282 | 51.5996 | Ireland | Butlerstown | substation
BVG | Ballyvallagh | -5.859 | 54.7842 | Ireland | Ballyvallagh | substation
BVK | Ballyvouskill | -9.0751 | 52.0198 | Ireland | Ballyvouskill | substation
BWR | Ballywater | -6.2555 | 52.5347 | Ireland | Ballywater | substation
BYC | Ballycronan More (Moyle) | -7.3055 | 53.7798 | Ireland | Ballycronan More (Moyle) | substation
BYH | Ballynahulla | -9.2579 | 52.1739 | Ireland | Ballynahulla | substation
CAB | Cabra | -6.3023 | 53.3674 | Ireland | Cabra | substation
CAE | CAES | -7.3055 | 53.7798 | Ireland | CAES | substation
CAG | Carrickalangan | -7.9352 | 54.8924 | Ireland | Carrickalangan | substation
CAH | Cahir | -7.9252 | 52.3745 | Ireland | Cahir | substation
CAM | Cam Cluster | -7.3055 | 53.7798 | Ireland | Cam Cluster | substation
CAR | Carnmoney | -5.9352 | 54.6737 | Ireland | Carnmoney | substation
CAS | Castlereagh | -5.8884 | 54.5757 | Ireland | Castlereagh | substation
CBG | Carrowbeg | -9.6341 | 53.9052 | Ireland | Carrowbeg | substation
CBL | Cloghboola | -9.0643 | 51.935 | Ireland | Cloghboola | substation
CBR | Castlebar | -9.2879 | 53.855 | Ireland | Castlebar | substation
CBT | Castlebagot | -6.4586 | 53.3165 | Ireland | Castlebagot | substation
CCN | Cloncreen | -7.1059 | 53.2709 | Ireland | Cloncreen | substation
CD | Carrigadrohid | -8.8611 | 51.9026 | Ireland | Carrigadrohid | substation
CDN | Carrigdangan | -9.1098 | 51.8038 | Ireland | Carrigdangan | substation
CDF | Carrickaduff | -6.772 | 54.076 | Ireland | Carrickaduff | substation
CDK | Castledockrill | -7.3055 | 53.7798 | Ireland | Castledockrill | substation
CDL | Cordal | -9.385 | 52.2181 | Ireland | Cordal | substation
CDU | Corduff | -6.3779 | 53.4012 | Ireland | Corduff | substation
CDY | Corderry | -6.5035 | 53.9389 | Ireland | Corderry | substation
CEN | Belfast Central | -5.9353 | 54.5733 | Ireland | Belfast Central | substation
CF | Cathaleen’s Fall | -8.1744 | 54.4995 | Ireland | Cathaleen’s Fall | substation
CFD | Clonfad | -7.3919 | 53.4189 | Ireland | Clonfad | substation
CFM | Castlefarm | -7.7302 | 52.9356 | Ireland | Castlefarm | substation
CGL | Coomagearlahy | -9.3168 | 51.9409 | Ireland | Coomagearlahy | substation
CH | Cahernagh | -8.9449 | 52.3162 | Ireland | Cahernagh | substation
CHA | Charleville | -8.684 | 52.3557 | Ireland | Charleville | substation
CHE | Cherrywood | -6.1421 | 53.2447 | Ireland | Cherrywood | substation
CHR | Cahernagh | -8.9449 | 52.3162 | Ireland | Cahernagh | substation
CKG | Corkagh | -6.4202 | 53.3065 | Ireland | Corkagh | substation
CKM | Carrickmines | -6.1829 | 53.2472 | Ireland | Carrickmines | substation
CKN | Clonkeen | -7.5646 | 54.053 | Ireland | Clonkeen | substation
CL | Cliff | -8.006 | 51.8266 | Ireland | Cliff | substation
CLA | Clashavoon | -7.3055 | 53.7798 | Ireland | Clashavoon | substation
CLD | Coolderrig | -7.3055 | 53.7798 | Ireland | Coolderrig | substation
CLE | Clonee | -6.4426 | 53.4106 | Ireland | Clonee | substation
CLG | Cloghran | -6.3559 | 53.4122 | Ireland | Cloghran | substation
CLH | Clahane | -9.4108 | 52.9388 | Ireland | Clahane | substation
CLM | Culmore_RD | -7.2865 | 55.0337 | Ireland | Culmore_RD | substation
CLN | Cloon | -8.7881 | 53.0838 | Ireland | Cloon | substation
CLO | Clogher | -7.1645 | 54.4143 | Ireland | Clogher | substation
CLS | Clonshaugh | -6.212 | 53.4144 | Ireland | Clonshaugh | substation
CLW | Carlow | -6.9325 | 52.8359 | Ireland | Carlow | substation
CNB | Coolnabacky | -7.1885 | 52.9767 | Ireland | Coolnabacky | substation
CNG | Coolnanoonag | -9.4253 | 52.5731 | Ireland | Coolnanoonag | substation
CNF | Caraunduff | -8.8137 | 53.2989 | Ireland | Caraunduff | substation
CNN | Croaghnagawna | -7.9017 | 54.7336 | Ireland | Croaghnagawna | substation
COL (I) | College Park | -7.2694 | 52.6405 | Ireland | College Park | substation
COL (N) | Coleraine | -6.6646 | 55.1326 | Ireland | Coleraine | substation
COO | Cookstown | -6.7444 | 54.6418 | Ireland | Cookstown | substation
COR | Corraclassy | -7.744 | 54.1491 | Ireland | Corraclassy | substation
COS | Carrick-on- Shannon | -8.0864 | 53.9452 | Ireland | Carrick-on- Shannon | substation
COW | Cow Cross | -7.3055 | 53.7798 | Ireland | Cow Cross | substation
CPK | Central Park | -8.0921 | 53.9451 | Ireland | Central Park | substation
CPS | Coolkeeragh Power Station | -7.2499 | 55.0439 | Ireland | Coolkeeragh Pow- er Station | substation
CRA | Crane | -8.2439 | 53.4129 | Ireland | Crane | substation
CRD | Croaghonagh | -7.8949 | 54.743 | Ireland | Croaghonagh | substation
CRE | Cregagh | -7.3055 | 53.7798 | Ireland | Cregagh | substation
CRG | Creagh | -8.2085 | 53.3369 | Ireland | Creagh | substation
CRH | Cruiserath | -6.3746 | 53.4167 | Ireland | Cruiserath | substation
CRM | Cromcastle | -6.2178 | 53.3931 | Ireland | Cromcastle | substation
CRN | Croaghaun | -10.1933 | 53.9786 | Ireland | Croaghaun | substation
CRO | Coolroe | -9.7372 | 52.02 | Ireland | Coolroe | substation
CRR | Curragha | -6.4437 | 53.5373 | Ireland | Curragha | substation
CRY | Crory | -7.3055 | 53.7798 | Ireland | Crory | substation
CSH | Cashla | -8.86 | 53.3172 | Ireland | Cashla | substation
CTG | Coomataggart | -9.3056 | 51.8654 | Ireland | Coomataggart | substation
CTN | Cauteen | -8.1814 | 52.5393 | Ireland | Cauteen | substation
CTY | City West | -6.4214 | 53.2821 | Ireland | City West | substation
CUL | Cullenagh | -6.998 | 52.9274 | Ireland | Cullenagh | substation
CUN | Cunghill | -8.6522 | 54.111 | Ireland | Cunghill | substation
CUR | Cureeny | -8.2439 | 53.4129 | Ireland | Cureeny | substation
CUS | Cushaling | -7.0246 | 53.2866 | Ireland | Cushaling | substation
CVW | Castleview | -8.6041 | 52.3192 | Ireland | Castleview | substation
DAL | Dallow | -7.3055 | 53.7798 | Ireland | Dallow | substation
DRN | Darndale | -6.1923 | 53.3983 | Ireland | Darndale | substation
DDK | Dundalk | -6.406 | 53.9979 | Ireland | Dundalk | substation
DEE | Deenes | -6.4368 | 53.636 | Ireland | Deenes | substation
DER | Derryiron | -7.228 | 53.3693 | Ireland | Derryiron | substation
DEY | Derrycarney | -8.0706 | 52.8706 | Ireland | Derrycarney | substation
DFR | Dunfirth | -6.8349 | 53.3964 | Ireland | Dunfirth | substation
DGN | Dungarvan | -7.6204 | 52.0937 | Ireland | Dungarvan | substation
DHN | Derrylahan | -8.0337 | 53.3529 | Ireland | Derrylahan | substation
DJG | Drombeg | -8.8925 | 51.5934 | Ireland | Drombeg | substation
DLN | Derrylyn | -7.5714 | 54.1962 | Ireland | Derrylyn | substation
DLT | Dalton | -7.3055 | 53.7798 | Ireland | Dalton | substation
DMY | Dunmanway | -9.1118 | 51.7223 | Ireland | Dunmanway | substation
DON | Donegall | -8.1096 | 54.6538 | Ireland | Donegall | substation
DOO | Doon | -8.2485 | 52.6043 | Ireland | Doon | substation
DRM | Drumkeen | -7.7514 | 54.866 | Ireland | Drumkeen | substation
DRN | Darndale | -6.1923 | 53.3983 | Ireland | Darndale | substation
DRO | Dromada | -9.1663 | 52.4506 | Ireland | Dromada | substation
DRO (N) | Dromore | -6.1494 | 54.4145 | Ireland | Dromore | substation
DRQ | Drumquin Cluster | -7.4889 | 54.6153 | Ireland | Drumquin Cluster | substation
DRU (I) | Drumline | -8.8511 | 52.7345 | Ireland | Drumline | substation
DRU (N) | Drumnakelly | -7.1702 | 54.6038 | Ireland | Drumnakelly | substation
DRY | Drybridge | -6.4016 | 53.7242 | Ireland | Drybridge | substation
DSN | Dunstown | -6.6902 | 53.1517 | Ireland | Dunstown | substation
DTN | Dardistown | -6.2339 | 53.4139 | Ireland | Dardistown | substation
DUN | Dungannon | -6.7669 | 54.5083 | Ireland | Dungannon | substation
DYN | Derrybrien | -8.6115 | 53.0658 | Ireland | Derrybrien | substation
EDE | Eden | -5.7581 | 54.729 | Ireland | Eden | substation
ENN (I) | Ennis | -8.9887 | 52.8474 | Ireland | Ennis | substation
ENN (N) | Enniskillen | -7.6315 | 54.3438 | Ireland | Enniskillen | substation
FAS | Fassaroe | -6.1471 | 53.1972 | Ireland | Fassaroe | substation
FAS E | Fassaroe East | -6.1471 | 53.1972 | Ireland | Fassaroe East | substation
FGH | Firlough | -7.3055 | 53.7798 | Ireland | Firlough | substation
FIN (I) | Finglas | -6.2984 | 53.3903 | Ireland | Finglas | substation
FIN (N) | Finaghy | -5.9803 | 54.5627 | Ireland | Finaghy | substation
FLA | Flagford | -8.1175 | 53.9094 | Ireland | Flagford | substation
FNT | Finnstown | -6.4628 | 53.3414 | Ireland | Finnstown | substation
FRN | Francis Street | -6.3473 | 53.7174 | Ireland | Francis Street | substation
GAE | Glanlee | -7.3055 | 53.7798 | Ireland | Glanlee | substation
GAL | Galway | -9.0513 | 53.274 | Ireland | Galway | substation
GRV | Garvagh | -6.6876 | 54.9833 | Ireland | Garvagh | substation
GCA | Grange Castle | -7.5427 | 52.6625 | Ireland | Grange Castle | substation
GGO | Glanagow | -8.2493 | 51.8125 | Ireland | Glanagow | substation
GI | Great Island | -8.28 | 51.8686 | Ireland | Great Island | substation
GIL | Gilra | -7.3055 | 53.7798 | Ireland | Gilra | substation
GLA | Glasmore | -6.2385 | 53.4678 | Ireland | Glasmore | substation
GLE (I) | Glenlara | -9.0781 | 52.2228 | Ireland | Glenlara | substation
GLE (N) | Glengormley | -5.9594 | 54.6798 | Ireland | Glengormley | substation
GLN | Glen | -8.5494 | 52.5928 | Ireland | Glen | substation
GAN | Gallanstown | -6.3672 | 53.3283 | Ireland | Gallanstown | substation
GLR | Glenree | -8.2944 | 54.7468 | Ireland | Glenree | substation
GOL | Golagh | -8.0539 | 54.544 | Ireland | Golagh | substation
GOR (I) | Gorman | -6.6358 | 53.6992 | Ireland | Gorman | substation
GOR (N) | Gort Cluster | -8.8187 | 53.0666 | Ireland | Gort Cluster | substation
GRA | Grange | -8.5274 | 54.3991 | Ireland | Grange | substation
GRH | Garballagh | -6.4567 | 53.6526 | Ireland | Garballagh | substation
GRI | Griffinrath | -6.574 | 53.3489 | Ireland | Griffinrath | substation
GRO | Garrow | -8.7597 | 53.9092 | Ireland | Garrow | substation
GWE | Gortawee | -7.5748 | 54.1291 | Ireland | Gortawee | substation
HAN | Hannastown | -6.031 | 54.5815 | Ireland | Hannastown | substation
HAR | Harolds Cross | -6.2811 | 53.3267 | Ireland | Harolds Cross | substation
HEU | Heuston Square | -6.3133 | 53.3425 | Ireland | Heuston Square | substation
HN | Huntstown | -6.342 | 53.413 | Ireland | Huntstown | substation
HRR | Harristown | -6.2875 | 53.4213 | Ireland | Harristown | substation
IA | Inniscarra | -8.6173 | 51.8949 | Ireland | Inniscarra | substation
IKE | Ikerrin | -7.3055 | 53.7798 | Ireland | Ikerrin | substation
INC | Inchicore | -6.3264 | 53.3359 | Ireland | Inchicore | substation
ISH | Irishtown | -6.2194 | 53.3375 | Ireland | Irishtown | substation
KBY | Kilbarry | -8.4743 | 51.928 | Ireland | Kilbarry | substation
KBY2 | Kilbarry No. 2 | -9.1144 | 51.7188 | Ireland | Kilbarry No. 2 | substation
KCR | Knockacummer | -9.0902 | 52.2593 | Ireland | Knockacummer | substation
KCY | Kilcarbery | -6.435 | 53.3132 | Ireland | Kilcarbery | substation
KDN | Kildonan | -6.3186 | 53.4034 | Ireland | Kildonan | substation
KEL | Kells | -6.877 | 53.7272 | Ireland | Kells | substation
KLC | Kells Cluster | -6.877 | 53.7272 | Ireland | Kells Cluster | substation
KER | Knockearagh | -8.9701 | 52.3061 | Ireland | Knockearagh | substation
KHL | Kill Hill | -7.6383 | 55.2291 | Ireland | Kill Hill | substation
KIN | Kinnegad | -7.105 | 53.4568 | Ireland | Kinnegad | substation
KKY | Kilkenny | -7.2464 | 52.6549 | Ireland | Kilkenny | substation
KLH | Knockalough | -9.2655 | 52.7188 | Ireland | Knockalough | substation
KLM | Kilmore | -6.2194 | 53.3927 | Ireland | Kilmore | substation
KLN | Killonan | -8.5354 | 52.6446 | Ireland | Killonan | substation
KLS | Kellis | -7.3055 | 53.7798 | Ireland | Kellis | substation
KMA | Knocknamona | -7.7291 | 54.9646 | Ireland | Knocknamona | substation
KMT | Killymallaght | -7.3459 | 54.9255 | Ireland | Killymallaght | substation
KNO | Knock | -8.9215 | 53.7901 | Ireland | Knock | substation
KNR | Knockanure | -9.3708 | 52.4659 | Ireland | Knockanure | substation
KNV | Knockavanna | -7.3055 | 53.7798 | Ireland | Knockavanna | substation
KNY | Knockranny | -9.504 | 53.8022 | Ireland | Knockranny | substation
KPG | Kilpaddoge | -9.392 | 52.5794 | Ireland | Kilpaddoge | substation
KPN | Killinaparson | -7.6016 | 53.113 | Ireland | Killinaparson | substation
KPS | Kilroot Power Station | -5.7677 | 54.7256 | Ireland | Kilroot Power Station | substation
KRA | Knockraha | -8.3401 | 51.9579 | Ireland | Knockraha | substation
KSE | Kishoge | -6.431 | 53.3337 | Ireland | Kishoge | substation
KTL | Kilteel | -6.5215 | 53.236 | Ireland | Kilteel | substation
KTN | Killoteran | -7.205 | 52.2402 | Ireland | Killoteran | substation
KUD | Kilmahud | -6.4261 | 53.3273 | Ireland | Kilmahud | substation
KUR | Knockumber | -6.7214 | 53.6543 | Ireland | Knockumber | substation
KYT | Kellystown | -6.4153 | 53.3792 | Ireland | Kellystown | substation
LA | Lanesboro | -7.9889 | 53.6726 | Ireland | Lanesboro | substation
LAR | Larne | -5.8236 | 54.8578 | Ireland | Larne | substation
LET | Letterkenny | -7.7343 | 54.9558 | Ireland | Letterkenny | substation
LIB | Liberty Street | -8.4784 | 51.8982 | Ireland | Liberty Street | substation
LIM (I) | Limerick | -8.6267 | 52.6638 | Ireland | Limerick | substation
LIM (N) | Limavady | -6.9337 | 55.0455 | Ireland | Limavady | substation
LIS (I) | Lisdrum | -6.3488 | 54.1634 | Ireland | Lisdrum | substation
LIS (N) | Lisburn | -6.058 | 54.5162 | Ireland | Lisburn | substation
LMR | Lisaghmore | -7.3036 | 54.98 | Ireland | Lisaghmore | substation
LNA | Lenalea | -7.8473 | 54.9037 | Ireland | Lenalea | substation
LOG | Loguestown | -6.6537 | 55.1441 | Ireland | Loguestown | substation
LOU | Louth | -6.5407 | 53.9508 | Ireland | Louth | substation
LPT | Longpoint | -8.2439 | 53.4129 | Ireland | Longpoint | substation
LSN | Lisheen | -9.3772 | 51.5307 | Ireland | Lisheen | substation
LUM | Lumcloon | -7.63 | 53.1198 | Ireland | Lumcloon | substation
LWD | Lodgewood | -6.5326 | 52.5844 | Ireland | Lodgewood | substation
MAC | Macroom | -8.9588 | 51.9048 | Ireland | Macroom | substation
MAG | Magherafelt | -6.608 | 54.7554 | Ireland | Magherafelt | substation
MAL | Mallow | -8.6539 | 52.139 | Ireland | Mallow | substation
MAY | Maynooth | -6.5918 | 53.3813 | Ireland | Maynooth | substation
MCD | McDermott | -7.3055 | 53.7798 | Ireland | McDermott | substation
MCE | Macetown | -6.5021 | 53.574 | Ireland | Macetown | substation
MEE | Meentycat | -7.8452 | 54.8706 | Ireland | Meentycat | substation
MEN | Monatooreen | -8.3112 | 51.9871 | Ireland | Monatooreen | substation
MHL | Misery Hill | -6.2396 | 53.3444 | Ireland | Misery Hill | substation
MID | Midleton | -8.1726 | 51.9143 | Ireland | Midleton | substation
MIL | Milltown | -6.248 | 53.3106 | Ireland | Milltown | substation
MKL | Magherakeel Cluster | -7.7191 | 54.6658 | Ireland | Magherakeel Cluster | substation
MLC | Mountlucas | -6.6796 | 52.8913 | Ireland | Mountlucas | substation
MLG | Mully Graffy | -7.3055 | 53.7798 | Ireland | Mully Graffy | substation
MLN | Mullagharlin | -6.3983 | 53.9733 | Ireland | Mullagharlin | substation
MON | Monread | -6.6526 | 53.2279 | Ireland | Monread | substation
MOY | Moy | -6.691 | 54.4466 | Ireland | Moy | substation
MP | Moneypoint | -9.4269 | 52.6085 | Ireland | Moneypoint | substation
MR | Marina | -7.3055 | 53.7798 | Ireland | Marina | substation
MRY | Mulreavy | -7.3055 | 53.7798 | Ireland | Mulreavy | substation
MTH | Meath Hill | -6.7218 | 53.8887 | Ireland | Meath Hill | substation
MTN | Moneteen | -8.6887 | 52.6341 | Ireland | Moneteen | substation
MUC | Muckerstown | -6.3855 | 53.4785 | Ireland | Muckerstown | substation
MUL | Mullingar | -7.3381 | 53.5259 | Ireland | Mullingar | substation
MUN | Mungret | -8.6935 | 52.6357 | Ireland | Mungret | substation
NAN (I) | Nangor | -6.4334 | 53.3214 | Ireland | Nangor | substation
NAR | Newtownards | -5.6932 | 54.5914 | Ireland | Newtownards | substation
NAV | Navan | -6.6967 | 53.6471 | Ireland | Navan | substation
NBY | Newbury | -6.2163 | 53.3997 | Ireland | Newbury | substation
NEN | Nenagh | -8.1976 | 52.8643 | Ireland | Nenagh | substation
NEW (I) | Newbridge | -6.8047 | 53.1751 | Ireland | Newbridge | substation
NEW (N) | Newry | -6.3402 | 54.1751 | Ireland | Newry | substation
NQS | North Quays | -6.4923 | 54.7877 | Ireland | North Quays | substation
NW | North Wall | -6.2377 | 53.3487 | Ireland | North Wall | substation
OLD | Oldcourt | -6.3384 | 53.2683 | Ireland | Oldcourt | substation
OMA | Omagh | -7.31 | 54.5977 | Ireland | Omagh | substation
ORL | Oriel | -7.3055 | 53.7798 | Ireland | Oriel | substation
OST | Oldstreet | -7.7058 | 53.2799 | Ireland | Oldstreet | substation
OUG | Oughtragh | -7.3055 | 53.7798 | Ireland | Oughtragh | substation
PA | Pollaphuca | -6.5853 | 53.1199 | Ireland | Pollaphuca | substation
PB | Poolbeg | -6.1878 | 53.34 | Ireland | Poolbeg | substation
PGN | Pigeon Top | -7.417 | 54.577 | Ireland | Pigeon Top | substation
PLA | Platin | -7.3055 | 53.7798 | Ireland | Platin | substation
PLS | Portlaoise | -7.2988 | 53.0328 | Ireland | Portlaoise | substation
POP | Poppintree | -6.2853 | 53.4002 | Ireland | Poppintree | substation
POT | Pottery Road | -6.1534 | 53.2734 | Ireland | Pottery Road | substation
PRO | Prospect | -8.7527 | 53.2946 | Ireland | Prospect | substation
PRT | Portan | -7.3055 | 53.7798 | Ireland | Portan | substation
PTN | Pelletstown | -6.3328 | 53.3743 | Ireland | Pelletstown | substation
RAF | Raffeen | -8.3723 | 51.8376 | Ireland | Raffeen | substation
RAT (I) | Rathkeale | -8.9404 | 52.5225 | Ireland | Rathkeale | substation
RAT (N) | Rathgael | -6.4244 | 53.3241 | Ireland | Rathgael | substation
RE | Ringsend | -6.2267 | 53.3419 | Ireland | Ringsend | substation
REM | Reamore | -9.5679 | 52.2916 | Ireland | Reamore | substation
RIC | Richmond | -8.2271 | 52.8767 | Ireland | Richmond | substation
RNW | Rinawade | -6.5142 | 53.3629 | Ireland | Rinawade | substation
ROP | Rosspile | -6.7457 | 52.2994 | Ireland | Rosspile | substation
ROS | Rosebank | -8.4507 | 51.8843 | Ireland | Rosebank | substation
RRU | Ratrussan | -7.1264 | 53.9964 | Ireland | Ratrussan | substation
RSK | Rasharkin Cluster | -6.4824 | 54.9569 | Ireland | Rasharkin Cluster | substation
RSY | Ringaskiddy | -8.3219 | 51.8304 | Ireland | Ringaskiddy | substation
RTO | Rathnaskillo | -7.3055 | 53.7798 | Ireland | Rathnaskillo | substation
RYB | Ryebrook | -6.5225 | 53.3777 | Ireland | Ryebrook | substation
SAL | Salthill | -9.0704 | 53.2626 | Ireland | Salthill | substation
SBH | Snughborough | -7.6046 | 54.13 | Ireland | Snughborough | substation
SCR | Screeb | -9.5556 | 53.3843 | Ireland | Screeb | substation
SH | Shannonbridge | -8.0447 | 53.2796 | Ireland | Shannonbridge | substation
SHE | Shelton Abbey | -6.1867 | 52.8177 | Ireland | Shelton Abbey | substation
SHL | Shellybanks | -6.2139 | 53.3328 | Ireland | Shellybanks | substation
SK | Sealrock | -9.0598 | 52.6324 | Ireland | Sealrock | substation
SKL | Shankill | -6.1238 | 53.2333 | Ireland | Shankill | substation
SKY | Srahnakilly | -9.5746 | 54.1576 | Ireland | Srahnakilly | substation
SLB | Sliabh Bawn | -8.0674 | 53.7289 | Ireland | Sliabh Bawn | substation
SLC | Slievecallan | -9.2707 | 52.8407 | Ireland | Slievecallan | substation
SLI | Sligo | -8.4761 | 54.2766 | Ireland | Sligo | substation
SLK | Slieve Kirk | -7.2639 | 54.9175 | Ireland | Slieve Kirk | substation
SNG | Singland | -8.5963 | 52.6563 | Ireland | Singland | substation
SOM | Somerset | -8.2305 | 53.2666 | Ireland | Somerset | substation
SOR | Sorne Hill | -7.3442 | 55.13 | Ireland | Sorne Hill | substation
SPR | Springtown | -7.8088 | 53.4638 | Ireland | Springtown | substation
SRA | Srananagh | -8.3927 | 54.1679 | Ireland | Srananagh | substation
STR (I) | Stratford | -6.6734 | 52.9879 | Ireland | Stratford | substation
STR (N) | Strabane | -7.4633 | 54.8274 | Ireland | Strabane | substation
SVN | Stevenstown | -6.197 | 53.597 | Ireland | Stevenstown | substation
SXH | Shantallow | -7.3161 | 55.0266 | Ireland | Shantallow | substation
TAN | Tandragee | -6.4148 | 54.3561 | Ireland | Tandragee | substation
TAW | Tawnaghmore | -8.7415 | 53.8017 | Ireland | Tawnaghmore | substation
TB | Tarbert | -9.3745 | 52.5725 | Ireland | Tarbert | substation
TBG | Trabeg | -10.2218 | 52.1197 | Ireland | Trabeg | substation
TBK | Tullabrack | -9.4794 | 52.6856 | Ireland | Tullabrack | substation
TEN | Timahoe | -7.2015 | 52.9607 | Ireland | Timahoe | substation
TGW | Terrygowan | -7.3055 | 53.7798 | Ireland | Terrygowan | substation
TH | Turlough Hill | -6.4164 | 53.0242 | Ireland | Turlough Hill | substation
THU | Thurles | -7.8044 | 52.6801 | Ireland | Thurles | substation
TIP | Tipperary | -8.1618 | 52.4736 | Ireland | Tipperary | substation
TIV | Tievebrack | -7.6384 | 54.7636 | Ireland | Tievebrack | substation
TLK | Trillick | -7.4872 | 54.4517 | Ireland | Trillick | substation
TLY | Tanley | -8.3833 | 54.4261 | Ireland | Tanley | substation
TMN | Tamnamore | -6.646 | 54.4925 | Ireland | Tamnamore | substation
TON | Tonroe | -8.3628 | 53.915 | Ireland | Tonroe | substation
TRE | Tremoge Cluster | -6.9792 | 54.5955 | Ireland | Tremoge Cluster | substation
TRI | Trien | -8.5532 | 53.7321 | Ireland | Trien | substation
TRL | Tralee | -9.6999 | 52.2713 | Ireland | Tralee | substation
TRN | Trinity | -8.2439 | 53.4129 | Ireland | Trinity | substation
TSB | Thornsberry | -7.3055 | 53.7798 | Ireland | Thornsberry | substation
TTU | Tullabeg | -6.3867 | 52.6151 | Ireland | Tullabeg | substation
TUR | Turleenan | -6.681 | 54.4653 | Ireland | Turleenan | substation
TYN | Tynagh | -8.3736 | 53.15 | Ireland | Tynagh | substation
UGL | Uggool | -9.86 | 53.6323 | Ireland | Uggool | substation
WAR | Waringstown | -6.3003 | 54.4352 | Ireland | Waringstown | substation
WAT | Waterford | -7.1101 | 52.2593 | Ireland | Waterford | substation
WEX | Wexford | -6.4633 | 52.3369 | Ireland | Wexford | substation
WH | Woodhouse | -7.6934 | 52.3378 | Ireland | Woodhouse | substation
WHI | Whitegate | -8.2321 | 51.8268 | Ireland | Whitegate | substation
WOL | Wolfe Tone | -8.2439 | 53.4129 | Ireland | Wolfe Tone | substation
YLW | Yellowmeadow | -7.3055 | 53.7798 | Ireland | Yellowmeadow | substation

## transmission system
Voltage (kV) |  |  |  | Length | Impedance on |  |  | Rating (MVA) |  |  |  | Voltage (kV) |  |  |  | Length (km) | Impedance on |  |  | Rating (MVA)
| From | To | No. | (km) | 100 MVA Base (pu) | [5 empty] | Action |  | From | To | No. |  | 100 MVA Base (pu) |  |  |  |  | Year
[5 empty] | R | X | B | Summer | Autumn | Winter | [6 empty] | R | X | B | Summer | Winter
400 | DSN | MP | 1 | 208.5 | 0 | 0.04 | 1.14 | 1283 | 1331 | 1454 | Add | 220 | BTN | CLE | 2 | 2.5 | 0.0001 | 0.0004 | 0.083 | 570 | 570 | 2021
400 | MP | OST | 1 | 104.14 | 0 | 0.03 | 0.49 | 1283 | 1331 | 1454 | Add | 220 | CDU | CRH | 2 |  | 4.8e-05 | 0.00018 | 0.0415 | 570 | 570 | 2021
400 | OST | WOO | 1 | 126 | 0 | 0.03 | 0.57 | 1577 | 1749 | 1944 | Add | 220 | CDU | CRH | 1 |  | 4.8e-05 | 0.00018 | 0.0415 | 570 | 570 | 2021
400 | WOO | WOO | 1 | 0.5 | 0 | 0 | 0.04 | 685 | 685 | 685 | Add | 220 | BRT | CLE | 1 | 2.5 | 0.0001 | 0.0004 | 0.083 | 570 | 570 | 2021
275 | BPS | HAN | 2 | 45.5 | 0 | 0.02 | 0.11 | 710 | 820 | 881 | Add | 110 | KUD | CBT | 1 | 0.75 | 0.0002 | 0.0009 | 0.0083 | 187 | 223 | 2021
275 | BPS | KEL | 1 | 34.5 | 0 | 0.01 | 0.09 | 710 | 820 | 881 | Add | 110 | DTN | BLC | 2 | 8 | 0.0041 | 0.00893 | 0.04864 | 140 | 143 | 2021
275 | BPS | MAG | 1 | 65.5 | 0 | 0.03 | 0.17 | 710 | 820 | 881 | Add | 110 | CKG | CBT | 2 | 0.75 | 0.0002 | 0.0009 | 0.0083 | 187 | 223 | 2021
275 | BPS | BYC | 1 | 0.8 | 0 | 0 | 0 | 710 | 820 | 881 | Amend | 110 | GCA | INC | 3 | 7.71 | 0.0047 | 0.0044 | 0.0939 | 124 | 124 | 2021
275 | CAS | HAN | 1 | 18.4 | 0 | 0.01 | 0.05 | 710 | 820 | 881 | Remove | 110 | GCA | KUD | 2 | 2.1 | 0.0015 | 0.0032 | 0.0211 | 140 | 140 | 2021
275 | CAS | HAN | 2 | 18.4 | 0 | 0.01 | 0.05 | 710 | 820 | 881 | Add | 110 | ADM | GCA | 1 | 2.5 | 0.0018 | 0.0038 | 0.0251 | 140 | 140 | 2021
275 | CAS | KPS | 1 | 66.8 | 0 | 0.03 | 0.17 | 710 | 820 | 881 | Remove | 110 | KIN | DFR | 1 | 29.25 | 0.0213 | 0.0957 | 0.0103 | 99 | 121 | 2021
275 | CAS | TAN | 1 | 45.6 | 0 | 0.02 | 0.11 | 710 | 820 | 881 | Add | 110 | KNY | BUF | 1 | 0.5 | 0.0002 | 0.0007 | 0.0056 | 140 | 140 | 2021
275 | CPS | MAG | 1 | 56.2 | 0.01 | 0.03 | 0.15 | 412 | 477 | 513 | Remove | 110 | KPG | TRL | 2 | 43.578 | 0.0271 | 0.1405 | 0.0231 | 178 | 190 | 2021
275 | CPS | MAG | 2 | 56.2 | 0.01 | 0.03 | 0.15 | 412 | 477 | 513 | Add | 110 | LIS | LIS | 1 | 0.25 | 0.0001 | 0.0003 | 0.0028 | 187 | 223 | 2021
275 | HAN | BYC | 1 | 44.7 | 0 | 0.02 | 0.11 | 710 | 820 | 881 | Remove | 110 | BKY | CKG | 1 | 3 | 0.0007 | 0.0033 | 0.033 | 187 | 223 | 2021
275 | KEL | KPS | 1 | 29 | 0 | 0.01 | 0.08 | 710 | 820 | 881 | Remove | 110 | BNK | INC | 1 | 10 | 0.0023 | 0.011 | 0.11 | 187 | 223 | 2021
275 | KEL | KPS | 2 | 29 | 0 | 0.01 | 0.08 | 710 | 820 | 881 | Amend | 110 | BNK | CBT | 1 | 1 | 0.0003 | 0.0011 | 0.011 | 187 | 223 | 2021
275 | KEL | MAG | 1 | 31.1 | 0 | 0.01 | 0.08 | 710 | 820 | 881 | Add | 110 | BKY | CBT | 2 | 0.6 | 0.0003 | 0.0011 | 0.011 | 187 | 223 | 2021
275 | KPS | TAN | 1 | 80.8 | 0 | 0.03 | 0.21 | 710 | 820 | 881 | Add | 110 | SXH | SOM | 1 | 45.45 | 0.0707 | 0.1563 | 0.0146 | 105 | 123 | 2021
275 | LOU | TAN | 1 | 50 | 0 | 0.02 | 0.13 | 710 | 820 | 881 | Remove | 110 | KRA | KRA | 1 |  | 0 | 0.0001 | 0 | 178 | 210 | 2021
275 | LOU | TAN | 2 | 50 | 0 | 0.02 | 0.13 | 710 | 820 | 881 | Remove | 110 | BOG | CRA | 1 | 24.677 | 0.0179 | 0.0811 | 0.0087 | 178 | 210 | 2021
275 | MAG | TMN | 1 | 25.68 | 0 | 0.01 | 0.07 | 710 | 820 | 881 | Remove | 110 | ADM | KUD | 1 |  | 0.00075 | 0.0016 | 0.01055 | 140 | 140 | 2021
275 | MAG | TMN | 2 | 25.68 | 0 | 0.01 | 0.07 | 710 | 820 | 881 | Add | 110 | BLE | KPG | 1 | 28.23 | 0.0178 | 0.0917 | 0.01 | 178 | 210 | 2021
275 | TAN | TMN | 1 | 25.74 | 0 | 0.01 | 0.07 | 710 | 820 | 881 | Add | 110 | AUG | BLE | 1 | 4.56 | 0.0029 | 0.0149 | 0.0017 | 178 | 210 | 2021
275 | TAN | TMN | 2 | 25.74 | 0 | 0.01 | 0.07 | 710 | 820 | 881 | Remove | 110 | AUG | KPG | 1 | 32.83 | 0.0207 | 0.1067 | 0.0116 | 178 | 210 | 2021
220 | AD | AD | 1 | 1.4 | 0 | 0 | 0.04 | 593 | 593 | 593 | Add | 110 | BLU | CDU | 1 | 18.33 | 0.0168 | 0.0557 | 0.0308 | 130 | 130 | 2021
220 | AD | GGO | 1 | 3.78 | 0 | 0 | 0.1 | 573 | 536 | 573 | Add | 110 | BLU | MUL | 1 | 56.18 | 0.079 | 0.1906 | 0.025 | 105 | 123 | 2021
220 | AD | KRA | 1 | 25.6 | 0 | 0.02 | 0.03 | 393 | 429 | 468 | Add | 110 | DJG | TRL | 1 | 32.333 | 0.0203 | 0.1047 | 0.0138 | 178 | 210 | 2021
220 | AD | KRA | 2 | 25.6 | 0 | 0.02 | 0.03 | 393 | 429 | 468 | Add | 110 | BLC | KLM | 1 | 4 | 0.0023 | 0.005 | 0.0291 | 140 | 140 | 2021
220 | AD | LPT | 1 | 0.97 | 0 | 0 | 0.03 | 593 | 593 | 593 | Add | 110 | DJG | KPG | 1 | 13.895 | 0.0081 | 0.0452 | 0.0104 | 178 | 210 | 2021
220 | AD | RAF | 1 | 14.4 | 0 | 0.01 | 0.25 | 434 | 481 | 513 | Add | 110 | BOG | TTU | 1 | 11.15 | 0.007 | 0.0362 | 0.0045 | 178 | 210 | 2021
220 | ARK | CKM | 1 | 53.61 | 0.01 | 0.05 | 0.08 | 434 | 481 | 513 | Add | 110 | CSH | SXH | 1 | 4.65 | 0.0073 | 0.016 | 0.0015 | 105 | 123 | 2021
220 | ARK | LWD | 1 | 39.02 | 0.01 | 0.03 | 0.05 | 434 | 481 | 513 | Remove | 110 | CSH | SOM | 1 | 50.019 | 0.0778 | 0.172 | 0.0161 | 99 | 121 | 2021
220 | BLC | FIN (I) | 1 | 10 | 0 | 0 | 0.33 | 570 | 570 | 570 | Add | 110 | CRA | TTU | 1 | 13.653 | 0.011 | 0.0452 | 0.0054 | 178 | 210 | 2021
220 | BVK | BYH | 1 | 28.57 | 0 | 0.03 | 0.05 | 434 | 473 | 513 | Remove | 110 | CDU | MUL | 1 | 73.255 | 0.09326 | 0.24155 | 0.03764 | 104 | 122 | 2021
220 | BVK | CLA | 1 | 16.78 | 0 | 0.01 | 0.03 | 740 | 769 | 792 | Add | 110 | KRA | MEN | 1 | 2.8 | 0.0017 | 0.0016 | 0.0341 | 124 | 124 | 2021
220 | CBT | INC | 1 | 14.3 | 0 | 0.01 | 0.01 | 761 | 780 | 794 | Add | 110 | BLC | GRA | 1 | 4.3 | 0.0025 | 0.0053 | 0.0309 | 140 | 140 | 2021
220 | CBT | INC | 2 | 14.32 | 0 | 0.01 | 0.02 | 761 | 780 | 794 | Add | 400 | KPG | MP | 1 | 6 | 0.00084 | 0.00023 | 0.54891 | 1210 | 1210 | 2022
220 | CBT | MAY | 1 | 11.72 | 0 | 0.01 | 0.02 | 761 | 780 | 794 | Add | 220 | ORL | ORL | 1 | 20.1 | 0.0007 | 0.0079 | 0.5502 | 593 | 593 | 2022
220 | CBT | MAY | 2 | 11.7 | 0 | 0.01 | 0.02 | 761 | 780 | 794 | Add | 220 | KYT | WOO | 1 | 13.8 | 0.003 | 0.0109 | 0.1124 | 761 | 746 | 2022
220 | CDU | FIN (I) | 1 | 3.73 | 0 | 0 | 0.01 | 434 | 481 | 513 | Add | 220 | KYT | MAY | 1 | 13.5 | 0.003 | 0.0106 | 0.112 | 761 | 746 | 2022
220 | CDU | FIN (I) | 2 | 3.73 | 0 | 0 | 0.01 | 434 | 481 | 513 | Remove | 220 | LOU | WOO | 1 | 61.2 | 0.0071 | 0.053 | 0.08 | 350 | 436 | 2022
220 | CDU | HN | 1 | 3.73 | 0 | 0 | 0.13 | 555 | 555 | 555 | Add | 220 | LOU | ORL | 1 | 14.5 | 0.0017 | 0.0126 | 0.019 | 434 | 513 | 2022
220 | CDU | WOO | 2 | 17.84 | 0 | 0.02 | 0.02 | 434 | 481 | 513 | Add | 220 | WOO | ORL | 1 | 49.2 | 0.0058 | 0.0427 | 0.0644 | 434 | 513 | 2022
220 | CKM | DSN | 1 | 41.61 | 0.01 | 0.04 | 0.11 | 434 | 481 | 513 | Add | 220 | ORL | ORL | 1 | 15.9 | 0.0007 | 0.0023 | 0.5279 | 570 | 570 | 2022
220 | CKM | ISH | 1 | 11.89 | 0 | 0.01 | 0.33 | 593 | 593 | 593 | Remove | 220 | FIN | SHL | 1 | 13.4 | 0.0005 | 0.0053 | 0.3668 | 536 | 557 | 2022
220 | CLA | KRA | 1 | 42.93 | 0.01 | 0.04 | 0.06 | 646 | 704 | 751 | Remove | 220 | MAY | WOO | 1 | 22.3 | 0.0027 | 0.0195 | 0.0295 | 350 | 436 | 2022
220 | CLE | CDU | 1 | 5.06 | 0 | 0 | 0.01 | 434 | 481 | 513 | Add | 220 | BLC | SHL | 1 | 23.4 | 0.001 | 0.0034 | 0.7769 | 570 | 570 | 2022
220 | CLE | WOO | 1 | 13.5 | 0 | 0.01 | 0.02 | 434 | 473 | 513 | Add | 110 | INC | YMW | 1 | 3.18 | 0.0008 | 0.0035 | 0.035 | 187 | 223 | 2022
220 | CSH | FLA | 1 | 88.09 | 0.01 | 0.08 | 0.12 | 350 | 393 | 436 | Add | 110 | BAL | DEE | 1 | 10.75 | 0.0068 | 0.0349 | 0.0044 | 178 | 210 | 2022
220 | CSH | PRO | 1 | 88.54 | 0.01 | 0.08 | 0.12 | 392 | 429 | 468 | Remove | 110 | BAL | DRY | 1 | 20 | 0.0126 | 0.065 | 0.0071 | 178 | 210 | 2022
220 | CSH | TYN | 1 | 39.89 | 0.01 | 0.03 | 0.06 | 761 | 777 | 792 | Add | 110 | BAG | CLG | 1 | 0.85 | 0.0002 | 0.001 | 0.0094 | 192 | 192 | 2022
220 | CUL | GI | 1 | 23.34 | 0 | 0.02 | 0.04 | 746 | 746 | 793 | Remove | 110 | BRO | RSK | 1 |  | 0.01 | 0.062 | 0.02 | 144 | 144 | 2022
220 | CUL | KRA | 1 | 86 | 0.01 | 0.07 | 0.12 | 646 | 704 | 765 | Add | 110 | GRV | RSK | 1 |  | 0.0098 | 0.059 | 0.0167 | 187 | 200 | 2022
220 | DSN | KLS | 1 | 59.3 | 0.01 | 0.05 | 0.08 | 393 | 429 | 468 | Add | 110 | BAG | SBH | 1 | 1.2 | 0.0003 | 0.0014 | 0.0133 | 192 | 192 | 2022
220 | DSN | MAY | 1 | 36.29 | 0 | 0.03 | 0.05 | 350 | 393 | 436 | Remove | 110 | CLG | FIN | 1 | 3.64 | 0.0035 | 0.0111 | 0.0073 | 124 | 124 | 2022
220 | DSN | MAY | 2 | 30.55 | 0 | 0.03 | 0.04 | 350 | 393 | 436 | Add | 110 | HRR | KIN | 1 | 5.825 | 0.006 | 0.0193 | 0.0034 | 136 | 159 | 2022
220 | DSN | TH | 1 | 26.62 | 0 | 0.02 | 0.14 | 351 | 351 | 351 | Add | 110 | GCA | YMW | 1 | 5.09 | 0.0012 | 0.0056 | 0.056 | 187 | 223 | 2022
220 | FIN (I) | HN | 1 | 1.4 | 0 | 0 | 0.04 | 593 | 593 | 593 | Add | 110 | GOR | GOR | 1 | 0.5 | 0.0002 | 0.0006 | 0.0056 | 187 | 223 | 2022
220 | FIN (I) | NW | 1 | 11.85 | 0 | 0 | 0.67 | 332 | 332 | 332 | Amend | 110 | GLN | PLA | 1 | 26.55 | 0.0167 | 0.0863 | 0.0094 | 178 | 210 | 2022
220 | FIN (I) | SHL | 1 | 13.4 | 0 | 0.01 | 0.37 | 536 | 557 | 557 | Add | 110 | HRR | DFR | 1 | 9.414 | 0.0064 | 0.0307 | 0.0034 | 104 | 157 | 2022
220 | FLA | LOU | 1 | 110.08 | 0.01 | 0.1 | 0.15 | 384 | 430 | 475 | Add | 110 | GI | ROP | 1 | 19.7 | 0.0123 | 0.0635 | 0.0103 | 178 | 210 | 2022
220 | FLA | SRA | 1 | 56.01 | 0.01 | 0.05 | 0.08 | 434 | 481 | 513 | Add | 110 | CKN | CUS | 1 | 0.5 | 0.0002 | 0.0007 | 0.0056 | 140 | 140 | 2022
220 | GGO | RAF | 1 | 9.5 | 0 | 0.01 | 0.41 | 570 | 570 | 570 | Add | 110 | FIN | MCE | 1 | 8.37 | 0.0081 | 0.0262 | 0.0127 | 124 | 124 | 2022
220 | GI | KLS | 1 | 70.43 | 0.01 | 0.06 | 0.1 | 393 | 429 | 468 | Remove | 110 | KIN | MUL | 1 | 24.919 | 0.0155 | 0.07731 | 0.02271 | 178 | 210 | 2022
220 | GI | LWD | 1 | 48.08 | 0.01 | 0.04 | 0.07 | 434 | 481 | 513 | Add | 110 | CFN | KIN | 1 | 6.59 | 0.0042 | 0.0215 | 0.0024 | 178 | 210 | 2022
220 | GOR | LOU | 1 | 32.41 | 0 | 0.03 | 0.04 | 434 | 473 | 476 | Add | 110 | CFN | MUL | 1 | 18.97 | 0.012 | 0.0617 | 0.0067 | 178 | 210 | 2022
220 | GOR | MAY | 1 | 42.19 | 0.01 | 0.04 | 0.06 | 350 | 393 | 436 | Remove | 110 | CKG | KUD | 1 | 0.75 | 0.0002 | 0.0009 | 0.0083 | 187 | 223 | 2022
220 | INC | ISH | 1 | 12.06 | 0 | 0.01 | 0.33 | 562 | 582 | 634 | Add | 110 | DRY | DEE | 1 | 9.55 | 0.006 | 0.031 | 0.004 | 178 | 210 | 2022
220 | INC | PB | 1 | 12.5 | 0 | 0 | 0.5 | 267 | 267 | 267 | Remove | 110 | CDU | PLA | 1 | 37 | 0.0233 | 0.1202 | 0.0131 | 178 | 210 | 2022
220 | INC | PB | 2 | 11.3 | 0 | 0 | 0.72 | 351 | 351 | 351 | Add | 110 | CDU | GLN | 1 | 11.05 | 0.007 | 0.0359 | 0.0039 | 178 | 210 | 2022
220 | ISH | SHL | 1 | 1.31 | 0 | 0 | 0.04 | 593 | 593 | 593 | Add | 110 | CLU | CBT | 1 | 0.1 | 0.0001 | 0.0002 | 0.0012 | 187 | 223 | 2022
220 | KLN | KPG | 1 | 70.57 | 0.01 | 0.06 | 0.11 | 434 | 481 | 513 | Add | 110 | CLU | KUD | 1 | 0.9 | 0.0003 | 0.001 | 0.01 | 187 | 223 | 2022
220 | KLN | KRA | 1 | 82.16 | 0.01 | 0.07 | 0.11 | 512 | 536 | 564 | Remove | 110 | GI | WEX | 1 | 34.5 | 0.0217 | 0.1121 | 0.0122 | 178 | 210 | 2022
220 | KLN | SH | 1 | 89.7 | 0.01 | 0.08 | 0.12 | 269 | 322 | 354 | Amend | 110 | AGN | CBT | 2 | 0.2 | 0.0001 | 0.0003 | 0.0022 | 187 | 223 | 2022
220 | KPG | KNR | 1 | 21.4 | 0 | 0.02 | 0.05 | 731 | 750 | 762 | Remove | 110 | SNU | MCE | 1 | 4.7271 | 0.0047 | 0.0151 | 0.0054 | 99 | 121 | 2022
220 | KPG | KNR | 2 | 20 | 0 | 0.01 | 0.97 | 731 | 750 | 762 | Add | 110 | BRO | AGI | 1 |  | 0.0027 | 0.0164 | 0.0047 | 144 | 144 | 2022
220 | KPG | MP | 1 | 5.4 | 0 | 0 | 0.24 | 660 | 660 | 660 | Add | 110 | AGN | CBT | 1 | 0.2 | 0.0001 | 0.0003 | 0.0022 | 187 | 223 | 2022
220 | KPG | MP | 2 | 5.4 | 0 | 0 | 0.24 | 660 | 660 | 660 | Add | 110 | ROP | WEX | 1 | 15.2 | 0.0095 | 0.0489 | 0.0087 | 178 | 210 | 2022
220 | KPG | TB | 1 | 2.8 | 0 | 0 | 0.03 | 350 | 393 | 436 | Add | 110 | THU | THU | 1 | 0.001 | 0.0001 | 0.0001 | 0.0001 | 218 | 232 | 2022
220 | KPG | TB | 2 | 2.8 | 0 | 0 | 0.03 | 350 | 393 | 436 | Remove | 275 | TAN | TMN | 1 |  | 0.00116 | 0.01085 | 0.0647 | 710 | 881 | 2025
220 | KNR | BYH | 1 | 37.79 | 0.01 | 0.03 | 0.06 | 434 | 473 | 513 | Add | 275 | TMN | TUR | 1 |  | 0.00024 | 0.00227 | 0.01354 | 710 | 881 | 2023
220 | KRA | RAF | 1 | 19.25 | 0 | 0.02 | 0.03 | 353 | 405 | 454 | Add | 275 | TAN | TUR | 2 |  | 0.00092 | 0.00862 | 0.05139 | 710 | 881 | 2023
220 | LOU | WOO | 1 | 61.2 | 0.01 | 0.05 | 0.08 | 350 | 393 | 436 | Remove | 275 | TAN | TMN | 2 |  | 0.00116 | 0.01085 | 0.0647 | 710 | 881 | 2023
220 | MAY | SH | 1 | 105.6 | 0.02 | 0.09 | 0.14 | 269 | 322 | 354 | Add | 275 | TMN | TUR | 2 |  | 0.00024 | 0.00227 | 0.01354 | 710 | 881 | 2023
220 | MAY | TH | 1 | 53.1 | 0.01 | 0.04 | 0.18 | 325 | 351 | 351 | Add | 275 | TAN | TUR | 1 |  | 0.00092 | 0.00862 | 0.05139 | 710 | 881 | 2023
220 | MAY | WOO | 1 | 22.3 | 0 | 0.02 | 0.03 | 350 | 393 | 436 | Add | 220 | GI | LWN | 1 | 0.4 | 0.0001 | 0.0002 | 0.011 | 593 | 593 | 2023
220 | MP | PRO | 1 | 12.7 | 0 | 0.01 | 0.02 | 537 | 600 | 663 | Add | 110 | AGT | CLM | 1 | 8 | 0.0084 | 0.0223 | 0.0502 | 200 | 200 | 2023
220 | NW | PB | 1 | 4.5 | 0 | 0 | 0.26 | 332 | 332 | 332 | Add | 110 | PLA | OBE | 1 | 2.955 | 0.0043 | 0.0096 | 0.0038 | 105 | 123 | 2023
220 | OST | TYN | 1 | 10.04 | 0 | 0.01 | 0.01 | 434 | 481 | 513 | Add | 110 | DGN | RTO | 1 | 15.475 | 0.0098 | 0.0502 | 0.006 | 178 | 210 | 2023
220 | PB | CKM | 1 | 14.5 | 0 | 0.01 | 0.58 | 267 | 267 | 267 | Remove | 110 | DRY | PLA | 1 | 5.3 | 0.0082 | 0.0182 | 0.0017 | 99 | 121 | 2023
220 | PB | PB | 1 | 1 | 0 | 0.04 | 0 | 450 | 450 | 450 | Add | 110 | DRY | OBE | 1 | 2.875 | 0.0042 | 0.0093 | 0.0038 | 105 | 123 | 2023
220 | PB | SHL | 1 | 0.12 | 0 | 0 | 0 | 593 | 593 | 593 | Add | 110 | KLC | KLC | 1 |  | 0.005 | 0.0312 | 0.00298 | 126 | 156 | 2023
220 | PRO | TB | 1 | 10.16 | 0 | 0.01 | 0.17 | 467 | 467 | 467 | Add | 110 | FGH | MOY | 1 | 15.87 | 0.0197 | 0.0472 | 0.048 | 105 | 123 | 2023
110 | AA | DRU | 1 | 18.15 | 0.03 | 0.06 | 0.01 | 99 | 110 | 121 | Add | 110 | CRR | CRR | 1 | 2 | 0.00059 | 0.00224 | 0.0156 | 80 | 50 | 2023
110 | AA | ENN (I) | 1 | 32.33 | 0.05 | 0.11 | 0.01 | 99 | 110 | 121 | Amend | 110 | CAS | FIN | 1 | 9.1 | 0.01369 | 0.03189 | 0.003 | 70 | 87 | 2023
110 | AA | LIM (I) | 1 | 11.7 | 0.01 | 0.04 | 0.01 | 178 | 194 | 209 |  |  |  | (N)
110 | AA | SNG | 1 | 5.46 | 0 | 0.02 | 0.01 | 145 | 161 | 177 | Remove | 110 | CUL | DGN | 1 | 34.239 | 0.0215 | 0.1093 | 0.0203 | 178 | 192 | 2023
110 | AD | WHI | 1 | 3.1 | 0.01 | 0.01 | 0 | 99 | 110 | 121 | Add | 110 | DLN | SH | 1 | 3.5 | 0.0009 | 0.0043 | 0.0386 | 140 | 140 | 2023
110 | ADM | INC | 1 | 10.5 | 0.01 | 0.03 | 0.02 | 103 | 123 | 134 | Add | 110 | CRR | PGN | 1 | 2.4 | 0.0017 | 0.00269 | 0.01872 | 60 | 60 | 2023
110 | AGH | ENN (N) | 1 | 31.1 | 0.04 | 0.1 | 0.02 | 109 | 114 | 124 | Add | 110 | MAY | TEN | 1 | 18.71 | 0.0118 | 0.0605 | 0.0093 | 112 | 112 | 2023
110 | AGL | DYN | 1 | 8 | 0.01 | 0.03 | 0 | 105 | 116 | 123 | Add | 110 | CD | KLP | 1 | 32.091 | 0.0202 | 0.1043 | 0.0113 | 178 | 210 | 2023
110 | AGL | ENN (I) | 1 | 38.2 | 0.06 | 0.13 | 0.01 | 99 | 110 | 121 | Remove | 110 | CD | KBY | 1 | 32.338 | 0.01988 | 0.1043 | 0.02497 | 178 | 209 | 2023
110 | AGL | SH | 1 | 45.88 | 0.07 | 0.16 | 0.02 | 104 | 113 | 119 | Add | 110 | GLE | KEL | 1 |  | 0.02726 | 0.06833 | 0.02722 | 82 | 90 | 2023
110 | AHA | KLN | 1 | 3.77 | 0 | 0.01 | 0 | 112 | 112 | 112 |  |  | (N)
110 | ANR | DOO | 1 | 2 | 0 | 0.01 | 0 | 105 | 116 | 123 | Add | 110 | KEL | KEL | 1 |  | 0.00033 | 0.00131 | 0.00798 | 144 | 144 | 2023
110 | ANT | KEL | 1 | 8.93 | 0.01 | 0.03 | 0 | 82 | 95 | 103 | Remove | 110 | GLR | MOY | 1 | 13.956 | 0.0216 | 0.048 | 0.0045 | 105 | 123 | 2023
110 | ANT | KEL | 2 | 8.93 | 0.01 | 0.03 | 0 | 82 | 95 | 103 | Add | 110 | CLD | GCA | 2 | 2.02 | 0.0005 | 0.0025 | 0.0223 | 140 | 140 | 2023
110 | AGY | TIV | 1 | 35 | 0.05 | 0.12 | 0.01 | 105 | 116 | 123 | Add | 110 | CUL | RTO | 1 | 19.175 | 0.0121 | 0.0622 | 0.0074 | 178 | 210 | 2023
110 | ARI | ARI | 1 | 0.21 | 0 | 0 | 0 | 105 | 116 | 123 | Add | 110 | LET | LNA | 1 | 12.23 | 0.0128 | 0.0408 | 0.0042 | 136 | 159 | 2023
110 | ARK | BEG | 1 | 21.94 | 0.01 | 0.08 | 0.01 | 99 | 111 | 122 | Remove | 110 | KBY | MAL | 1 | 29.2 | 0.0184 | 0.0949 | 0.0103 | 134 | 159 | 2023
110 | ARK | BOG | 1 | 29 | 0.02 | 0.1 | 0.01 | 178 | 197 | 210 | Remove | 110 | KBY | MR | 1 | 4.438 | 0.00448 | 0.01466 | 0.004 | 103 | 130 | 2023
110 | ARK | SHE | 2 | 2.2 | 0 | 0.01 | 0 | 34 | 46 | 57 | Remove | 110 | KBY | KRA | 2 | 12.5 | 0.0183 | 0.0428 | 0.0041 | 99 | 121 | 2023
110 | ART | FIN (I) | 1 | 9 | 0.01 | 0.01 | 0.06 | 120 | 120 | 131 | Add | 110 | TIV | MLG | 1 | 6.1 | 0.0044 | 0.0091 | 0.0612 | 140 | 140 | 2023
110 | ART | MCD | 1 | 4.9 | 0 | 0.01 | 0.03 | 120 | 120 | 131 | Remove | 110 | CAR | CAS | 1 |  | 0.03714 | 0.0875 | 0.00798 | 69 | 86 | 2023
110 | ARV | COS | 1 | 43.04 | 0.07 | 0.15 | 0.01 | 104 | 113 | 123 | Remove | 110 | CAR | CAS | 2 |  | 0.03695 | 0.08641 | 0.00803 | 70 | 87 | 2023
110 | ARV | GWE | 1 | 30.6 | 0.02 | 0.1 | 0.01 | 178 | 197 | 210 | Add | 110 | KLP | KRA | 2 | 12.5 | 0.0183 | 0.0428 | 0.0041 | 99 | 121 | 2023
110 | ARV | NAV | 1 | 65.5 | 0.04 | 0.21 | 0.02 | 178 | 197 | 210 | Remove | 110 | GOR | PLA | 1 | 19.732 | 0.0302 | 0.0681 | 0.0064 | 99 | 121 | 2023
110 | ARV | SKL | 1 | 18.52 | 0.01 | 0.06 | 0.01 | 178 | 197 | 210 | Add | 110 | GOR | GRH | 1 | 14.125 | 0.0214 | 0.0484 | 0.0051 | 105 | 123 | 2023
110 | ARV | SKL | 2 | 23.56 | 0.02 | 0.08 | 0.01 | 178 | 197 | 210 | Remove | 110 | DER | MAY | 1 | 43.448 | 0.0277 | 0.14567 | 0.0177 | 74 | 93 | 2023
110 | ATE | DRO | 1 | 5.47 | 0 | 0.01 | 0.06 | 120 | 124 | 140 | Add | 110 | AIR | ROS | 1 |  | 0.01312 | 0.03406 | 0.00338 | 82 | 103 | 2023
110 | ATE | KNR | 1 | 6.71 | 0 | 0.02 | 0.01 | 178 | 197 | 210 | Add | 110 | CLD | GCA | 1 | 1.87 | 0.0005 | 0.0023 | 0.0207 | 140 | 140 | 2023
110 | ATH | LA | 1 | 35.78 | 0.05 | 0.12 | 0.01 | 99 | 110 | 121 | Add | 110 | DER | TEN | 1 | 25.125 | 0.0158 | 0.0817 | 0.0089 | 178 | 210 | 2023
110 | ATH | SH | 1 | 21.63 | 0.01 | 0.07 | 0.01 | 178 | 190 | 190 | Add | 110 | CPS | CLM | 1 | 3.6 | 0.00101 | 0.0028 | 0.0867 | 200 | 200 | 2023
110 | BGD | INC | 1 | 6.5 | 0.01 | 0.01 | 0.07 | 140 | 140 | 140 | Add | 110 | BGT | KKY | 1 | 22 | 0.0139 | 0.0715 | 0.0078 | 178 | 210 | 2023
110 | BGD | INC | 2 | 6.5 | 0.01 | 0.01 | 0.07 | 140 | 140 | 140 | Amend | 110 | CAS | FIN | 1 | 9.1 | 0.01376 | 0.0323 | 0.003 | 69 | 86 | 2023
110 | ATY | CLW | 1 | 24.23 | 0.04 | 0.08 | 0.01 | 99 | 110 | 121 |  |  |  | (N)
110 | ATY | PLS | 1 | 25.48 | 0.04 | 0.09 | 0.01 | 99 | 110 | 121 | Add | 110 | LNA | TIV | 1 | 33.13 | 0.0345 | 0.1106 | 0.0113 | 136 | 159 | 2023
110 | AUG | CFM | 1 | 0.65 | 0 | 0 | 0 | 96 | 96 | 96 | Add | 110 | FGH | GLR | 1 | 5.701 | 0.0038 | 0.0122 | 0.0448 | 105 | 123 | 2023
110 | AUG | CFM | 2 | 0.67 | 0 | 0 | 0 | 96 | 96 | 96 | Add | 110 | GRH | PLA | 1 | 6.05 | 0.0094 | 0.0208 | 0.0025 | 105 | 123 | 2023
110 | AUG | KPG | 1 | 32.83 | 0.02 | 0.11 | 0.01 | 178 | 197 | 210 | Remove | 110 | LET | TIV | 1 | 45.2 | 0.0471 | 0.1508 | 0.0154 | 136 | 159 | 2023
110 | AUG | MTN | 1 | 27.5 | 0.02 | 0.09 | 0.01 | 178 | 197 | 210 | Add | 110 | KLP | MAL | 1 | 29.2 | 0.0184 | 0.0949 | 0.0103 | 134 | 159 | 2023
110 | AUG | SK | 3 | 1 | 0 | 0 | 0.01 | 120 | 120 | 120 | Add | 220 | DSN | MAY | 2 | 30.55 | 0.0036 | 0.0265 | 0.04 | 434 | 513 | 2024
110 | AUG | SK | 4 | 1 | 0 | 0 | 0.01 | 120 | 120 | 120 | Remove | 220 | DSN | MAY | 2 | 30.55 | 0.0036 | 0.0265 | 0.04 | 350 | 436 | 2024
110 | BAL | CDU | 1 | 15.93 | 0.01 | 0.06 | 0.01 | 178 | 194 | 209 | Add | 110 | BDM | MID | 1 | 3.516 | 0.0047 | 0.0122 | 0.0012 | 99 | 121 | 2024
110 | BAL | DRY | 1 | 20 | 0.01 | 0.07 | 0.01 | 178 | 197 | 210 | Add | 110 | BDM | WHI | 1 | 18.306 | 0.0268 | 0.0628 | 0.006 | 99 | 121 | 2024
110 | BAN | BRI | 1 | 2.6 | 0 | 0.01 | 0 | 105 | 116 | 123 | Add | 110 | BGT | CNB | 1 | 28 | 0.0176 | 0.091 | 0.0099 | 178 | 210 | 2024
110 | BAN | BRI | 2 | 2.5 | 0 | 0.01 | 0 | 99 | 110 | 121 | Add | 110 | KEL | RSK | 2 | 25.903 | 0.02167 | 0.1344 | 0.0129 | 188 | 213 | 2024
110 | BAN | DMY | 1 | 25.9 | 0.04 | 0.09 | 0.01 | 99 | 110 | 121 | Remove | 110 | ATY | PLS | 1 | 25.482 | 0.03822 | 0.08764 | 0.00848 | 99 | 121 | 2024
110 | BAN | RAF | 1 | 26.89 | 0.04 | 0.09 | 0.01 | 99 | 110 | 121 | Add | 110 | ARK | PHY | 2 | 2.38 | 0.0015 | 0.0078 | 0.0009 | 178 | 210 | 2024
110 | BAN | TAN | 1 | 18.4 | 0.02 | 0.06 | 0.01 | 82 | 95 | 103 | Add | 110 | MOY | TON | 1 | 58 | 0.0365 | 0.1884 | 0.0205 | 178 | 210 | 2024
110 | BAN | TAN | 2 | 18.4 | 0.02 | 0.05 | 0.01 | 82 | 95 | 103 | Remove | 110 | MID | WHI | 1 | 20.022 | 0.0303 | 0.0691 | 0.0065 | 99 | 121 | 2024
110 | BAR | BAR | 1 | 0.31 | 0 | 0 | 0 | 136 | 150 | 159 | Add | 110 | ATY | CNB | 1 | 21.94 | 0.0138 | 0.0713 | 0.0078 | 178 | 210 | 2024
110 | BCT | CKM | 1 | 3.1 | 0 | 0.01 | 0.03 | 140 | 140 | 140 | Add | 110 | AGN | KSE | 1 | 1.7 | 0.0004 | 0.0019 | 0.0188 | 187 | 223 | 2024
110 | BCT | COO | 1 | 15.1 | 0.01 | 0.05 | 0.03 | 130 | 130 | 130 | Add | 110 | ARK | PHY | 1 | 2.25 | 0.0015 | 0.0074 | 0.0008 | 178 | 210 | 2024
110 | BDA | MON | 1 | 11.2 | 0.01 | 0.03 | 0.03 | 99 | 110 | 121 | Add | 110 | BKY | KCY | 1 | 0.75 | 0.0002 | 0.0009 | 0.0083 | 187 | 223 | 2024
110 | BDA | NEW (I) | 1 | 7.2 | 0.01 | 0.02 | 0.03 | 122 | 122 | 122 | Add | 110 | GAR | GLN | 1 | 0.1 | 0.0001 | 0.0002 | 0.0012 | 140 | 140 | 2024
110 | BDN | CUL | 1 | 21.8 | 0.03 | 0.08 | 0.01 | 196 | 216 | 217 | Add | 110 | PHY | SHE | 1 | 0.375 | 0.0003 | 0.0013 | 0.0002 | 178 | 210 | 2024
110 | BDN | DOO | 1 | 11.3 | 0.01 | 0.04 | 0 | 178 | 197 | 210 | Remove | 110 | ARK | SHE | 2 | 2.2 | 0.0035 | 0.0077 | 0.0008 | 34 | 57 | 2024
110 | BEG | CKM | 1 | 32.3 | 0.02 | 0.12 | 0.01 | 136 | 150 | 159 | Add | 110 | CNB | PLS | 1 | 8.36 | 0.0051 | 0.0261 | 0.0083 | 178 | 210 | 2024
110 | BIN | CF | 1 | 34.26 | 0.05 | 0.12 | 0.01 | 99 | 110 | 121 | Add | 110 | CBT | KCY | 1 | 0.75 | 0.0002 | 0.0009 | 0.0083 | 187 | 223 | 2024
110 | BIN | TIV | 1 | 23.2 | 0.02 | 0.08 | 0.01 | 136 | 150 | 159 | Add | 110 | CBT | KSE | 1 | 1.9 | 0.0005 | 0.0021 | 0.021 | 187 | 223 | 2024
110 | BK | CBR | 1 | 37.39 | 0.05 | 0.13 | 0.01 | 195 | 202 | 221 | Add | 400 | TUR | WOO | 1 |  | 0.0027 | 0.0311 | 0.7066 | 1424 | 1731 | 2025
110 | BK | MOY | 1 | 27 | 0.02 | 0.09 | 0.01 | 178 | 197 | 210 | Add | 400 | CNB | MP | 1 |  | 0.0033 | 0.01134 | 0.858 | 1577 | 1944 | 2025
110 | BK | SKY | 1 | 4 | 0 | 0 | 0.04 | 192 | 192 | 192 | Remove | 400 | DSN | MP | 1 | 208.5 | 0.00405 | 0.04359 | 1.1397 | 1283 | 1454 | 2025
110 | BK | CRN | 1 | 3.3 | 0 | 0.01 | 0 | 178 | 197 | 210 | Add | 400 | CNB | DSN | 1 |  | 0.0009 | 0.003 | 0.226 | 1577 | 1944 | 2025
110 | BK | SKY | 1 | 4 | 0 | 0 | 0.04 | 187 | 206 | 223 | Add | 110 | CNB | CNB | 1 |  | 0 | 0.0001 | 0 | 178 | 210 | 2025
110 | BKM | CUR | 1 | 7.3 | 0 | 0.01 | 0.07 | 120 | 120 | 120 | Add | 110 | RSK | TGW | 1 |  | 0.01264 | 0.07231 | 0.03087 | 200 | 200 | 2026
110 | BLA | RE | 1 | 7.7 | 0 | 0.01 | 0.14 | 119 | 119 | 119 | Add | 110 | KEL | TGW | 1 |  | 0.0097 | 0.04125 | 0.00443 | 200 | 200 | 2026
110 | BLI | DMY | 1 | 27.57 | 0.04 | 0.09 | 0.01 | 105 | 116 | 123 | Remove | 110 | CRG | KEL | 1 |  | 0.02933 | 0.07667 | 0.01292 | 82 | 103 | 2026
110 | BLK | BLK | 1 | 0.5 | 0 | 0 | 0 | 136 | 150 | 159 | Add | 110 | CEN | CEN | 1 | 0.001 | 0.0001 | 0.0001 | 0.0001 | 187 | 223 | 2026
110 | BMA | KEL | 1 | 10 | 0.01 | 0.04 | 0 | 109 | 119 | 124 | Add | 110 | BNM | CEN | 1 |  | 0.00024 | 0.00093 | 0.00647 |  |  | 2026
110 | BMA | KEL | 2 | 11.5 | 0.02 | 0.04 | 0 | 109 | 119 | 124 | Add | 110 | CRG | TGW | 1 |  | 0.01276 | 0.034 | 0.00896 | 109 | 124 | 2026
110 | BNH | CAS | 1 | 21.2 | 0.03 | 0.07 | 0.01 | 82 | 95 | 103 | Add | 110 | GI | WAT | 2 | 12.901 | 0.0082 | 0.042 | 0.0046 | 178 | 210 | 2027
110 | BNH | CAS | 2 | 21.2 | 0.03 | 0.07 | 0.01 | 82 | 95 | 103
110 | BNK | CKG | 1 | 3 | 0 | 0 | 0.03 | 187 | 206 | 223
110 | BNK | INC | 1 | 10 | 0 | 0.01 | 0.11 | 187 | 206 | 223
110 | BNM | DON | 1 | 6.02 | 0.01 | 0.01 | 0.05 | 75 | 75 | 82
110 | BNM | DON | 2 | 5.81 | 0.01 | 0.01 | 0.05 | 75 | 75 | 82
110 | BGH | CLA | 1 | 13.5 | 0.01 | 0.04 | 0.03 | 178 | 197 | 210
110 | BOG | CRA | 1 | 24.67 | 0.02 | 0.08 | 0.01 | 178 | 197 | 210
110 | BOL | ENN | 1 | 24.69 | 0.02 | 0.08 | 0.01 | 178 | 197 | 210
110 | BOL | TBK | 1 | 18.28 | 0.01 | 0.06 | 0.01 | 178 | 197 | 210
110 | BPS | BVG | 1 | 17.3 | 0.02 | 0.06 | 0.01 | 82 | 95 | 103
110 | BPS | BVG | 2 | 17.3 | 0.02 | 0.06 | 0.01 | 82 | 95 | 103
110 | BPS | EDE | 1 | 15.1 | 0.02 | 0.05 | 0.01 | 69 | 80 | 86
110 | BPS | EDE | 2 | 15.1 | 0.02 | 0.05 | 0.01 | 70 | 81 | 87
110 | BRO | RSK | 1 | 17.44 | 0.01 | 0.06 | 0.02 | 144 | 144 | 144
110 | BRY | RAF | 1 | 1.7 | 0 | 0.01 | 0 | 63 | 82 | 92
110 | BRY | RAF | 2 | 1.8 | 0 | 0.01 | 0 | 99 | 110 | 121
110 | BUT | CUL | 1 | 12.32 | 0.01 | 0.04 | 0.01 | 178 | 192 | 192
110 | BUT | KTN | 1 | 2.72 | 0 | 0.01 | 0 | 200 | 209 | 216
110 | BVG | KEL | 1 | 21.2 | 0.03 | 0.07 | 0.01 | 109 | 119 | 124
110 | BVG | KEL | 2 | 20.3 | 0.03 | 0.07 | 0.01 | 109 | 119 | 124
110 | BVG | LAR | 1 | 7.1 | 0.01 | 0.02 | 0 | 79 | 79 | 113
110 | BVG | LAR | 2 | 7.1 | 0.01 | 0.02 | 0 | 79 | 79 | 113
110 | BVK | CTG | 1 | 31.7 | 0.01 | 0.04 | 0.39 | 228 | 228 | 228
110 | BWR | CRA | 1 | 22.4 | 0.01 | 0.02 | 0.14 | 115 | 115 | 115
110 | BYH | CDL | 1 | 9.54 | 0 | 0.01 | 0.11 | 195 | 201 | 220
110 | BYH | Gle | 1 | 19.1 | 0.01 | 0.02 | 0.19 | 124 | 124 | 124
110 | CAB | PTN | 1 | 2.66 | 0 | 0.01 | 0.01 | 80 | 105 | 119
110 | CAB | WOL | 1 | 4.7 | 0 | 0.01 | 0.03 | 120 | 120 | 131
110 | CAH | BAR | 1 | 43.69 | 0.07 | 0.15 | 0.01 | 105 | 116 | 123
110 | CAH | DOO | 1 | 15.73 | 0.01 | 0.05 | 0.01 | 178 | 197 | 210
110 | CAH | KHL | 1 | 17.95 | 0.01 | 0.06 | 0.01 | 178 | 197 | 210
110 | CAH | TIP | 1 | 18.06 | 0.01 | 0.06 | 0.01 | 178 | 197 | 210
110 | CAR | CAS | 1 | 24.7 | 0.04 | 0.09 | 0.01 | 69 | 80 | 86
110 | CAR | CAS | 2 | 24.7 | 0.04 | 0.09 | 0.01 | 70 | 81 | 87
110 | CAR | EDE | 1 | 12.4 | 0.02 | 0.04 | 0 | 69 | 80 | 86
110 | CAR | EDE | 2 | 12.4 | 0.02 | 0.04 | 0 | 69 | 80 | 86
110 | CAS | CRE | 1 | 2.96 | 0 | 0 | 0.06 | 132 | 132 | 145
110 | CAS | CRE | 2 | 2.96 | 0 | 0 | 0.06 | 132 | 132 | 145
110 | CAS | KNO | 1 | 4.59 | 0.01 | 0 | 0.04 | 66 | 66 | 73
110 | CAS | KNO | 2 | 4.52 | 0.01 | 0 | 0.04 | 66 | 66 | 73
110 | CAS | NAR | 1 | 18 | 0.02 | 0.04 | 0.07 | 109 | 109 | 124
110 | CAS | NAR | 2 | 19.8 | 0.02 | 0.05 | 0.07 | 109 | 124 | 124
110 | CAS | RAT (N) | 1 | 18.9 | 0.03 | 0.06 | 0.01 | 82 | 95 | 103
110 | CAS | RAT (N) | 2 | 18.9 | 0.03 | 0.06 | 0.01 | 82 | 95 | 103
110 | CAS | ROS | 1 | 1.83 | 0 | 0 | 0.02 | 144 | 144 | 152
110 | CAS | ROS | 2 | 1.83 | 0 | 0 | 0.02 | 144 | 144 | 152
110 | CAU | KLN | 1 | 29.24 | 0.02 | 0.1 | 0.01 | 178 | 197 | 210
110 | KNG | TRI | 1 | 13.62 | 0.01 | 0.02 | 0.1 | 124 | 124 | 124
110 | CBG | CBR | 1 | 26.71 | 0.04 | 0.08 | 0.06 | 99 | 110 | 121
110 | CBR | CLN | 1 | 57.52 | 0.09 | 0.2 | 0.02 | 99 | 110 | 121
110 | CBR | DLT | 1 | 27.77 | 0.04 | 0.1 | 0.01 | 99 | 110 | 121
110 | CCF | CAD | 1 | 5.5 | 0 | 0.01 | 0.06 | 140 | 140 | 140
110 | CCF | CKL | 1 | 7 | 0 | 0.01 | 0.08 | 140 | 140 | 140
110 | CD | KBY | 1 | 32.33 | 0.02 | 0.1 | 0.03 | 178 | 194 | 209
110 | CD | MAC | 1 | 2.41 | 0 | 0.01 | 0 | 178 | 197 | 210
110 | CDK | LWD | 1 | 8.4 | 0 | 0.01 | 0.05 | 115 | 115 | 115
110 | CDU | MUL | 1 | 73.26 | 0.09 | 0.24 | 0.04 | 104 | 113 | 122
110 | CDU | PLA | 1 | 37 | 0.02 | 0.12 | 0.01 | 178 | 197 | 210
110 | CDU | RYB | 1 | 13 | 0.01 | 0.04 | 0 | 178 | 197 | 219
110 | CDU | SBH | 1 | 1.77 | 0 | 0 | 0.02 | 238 | 238 | 238
110 | CDY | ARI | 1 | 13.68 | 0.01 | 0.04 | 0.01 | 178 | 197 | 210
110 | CDY | GRV | 1 | 5.83 | 0 | 0.02 | 0 | 132 | 137 | 150
110 | CDY | SRA | 1 | 12.7 | 0.02 | 0.04 | 0 | 178 | 197 | 210
110 | CEN | CRE | 1 | 3.22 | 0 | 0 | 0.03 | 144 | 144 | 144
110 | CEN | CRE | 2 | 3.22 | 0 | 0 | 0.03 | 144 | 144 | 144
110 | CF | CL | 1 | 5.5 | 0.01 | 0.02 | 0 | 136 | 150 | 159
110 | CF | CLO | 2 | 25.74 | 0.04 | 0.09 | 0.01 | 178 | 194 | 209
110 | CF | COR | 1 | 61.3 | 0.04 | 0.2 | 0.02 | 178 | 194 | 209
110 | CF | SRA | 1 | 52.98 | 0.07 | 0.18 | 0.02 | 196 | 214 | 234
110 | CF | CLO | 1 | 26.07 | 0.02 | 0.09 | 0.02 | 178 | 194 | 209
110 | CF | SRA | 2 | 49.2 | 0.03 | 0.16 | 0.02 | 178 | 197 | 210
110 | CGL | GAE | 1 | 2 | 0 | 0 | 0.01 | 130 | 130 | 130
110 | CHA | GLE | 1 | 28.06 | 0.04 | 0.1 | 0.01 | 99 | 110 | 121
110 | CHA | KLN | 1 | 36.9 | 0.04 | 0.12 | 0.01 | 136 | 150 | 159
110 | CHA | MAL | 1 | 22.5 | 0.01 | 0.07 | 0.01 | 178 | 197 | 210
110 | CHE | FAS | 1 | 2.2 | 0 | 0.01 | 0 | 105 | 116 | 123
110 | CKG | CBT | 1 | 0.75 | 0 | 0 | 0.01 | 187 | 206 | 223
110 | CKG | KUD | 1 | 0.75 | 0 | 0 | 0.01 | 187 | 206 | 223
110 | CKM | CHE | 1 | 4 | 0 | 0.01 | 0.03 | 105 | 116 | 123
110 | CKM | COO | 2 | 16 | 0.01 | 0.04 | 0.06 | 130 | 130 | 130
110 | CKM | FAS | 1 | 2.9 | 0.01 | 0.01 | 0 | 105 | 116 | 123
110 | CKM | FAS | 1 | 7.5 | 0.01 | 0.03 | 0 | 105 | 116 | 123
110 | CKM | POT | 1 | 3.2 | 0 | 0 | 0.06 | 119 | 119 | 119
110 | CKN | CGL | 1 | 6.3 | 0 | 0.02 | 0 | 178 | 190 | 190
110 | CKN | GRO | 1 | 15.17 | 0.01 | 0.01 | 0.14 | 120 | 120 | 120
110 | CKN | KER | 1 | 20.3 | 0.01 | 0.07 | 0.01 | 178 | 197 | 210
110 | CLA | CKN | 1 | 29.97 | 0.02 | 0.1 | 0.02 | 178 | 190 | 190
110 | CLA | DMY | 1 | 38.83 | 0.02 | 0.13 | 0.02 | 178 | 197 | 210
110 | CLA | MAC | 1 | 5.66 | 0 | 0.02 | 0 | 161 | 176 | 191
110 | CLA | MAC | 2 | 5.66 | 0 | 0.01 | 0.1 | 161 | 176 | 192
110 | CLG | CDU | 1 | 2.5 | 0 | 0 | 0.03 | 187 | 206 | 219
110 | CLG | FIN (I) | 1 | 3.64 | 0 | 0.01 | 0.01 | 124 | 124 | 124
110 | CLH | TRI | 1 | 9 | 0.01 | 0.03 | 0 | 99 | 110 | 121
110 | CLH | TRL | 1 | 13.5 | 0.02 | 0.05 | 0.01 | 105 | 114 | 123
110 | CLN | LA | 1 | 64.76 | 0.1 | 0.22 | 0.02 | 99 | 110 | 121
110 | CLO | CCF | 1 | 18 | 0.01 | 0.06 | 0.01 | 178 | 197 | 210
110 | CLO | GL | 1 | 0.25 | 0 | 0 | 0 | 187 | 206 | 217
110 | CLO | MRY | 1 | 7.68 | 0 | 0.01 | 0.09 | 136 | 136 | 136
110 | CLW | KLS | 1 | 5.4 | 0.01 | 0.02 | 0 | 99 | 110 | 121
110 | CLW | KLS | 2 | 5.28 | 0.01 | 0.02 | 0 | 99 | 110 | 121
110 | CLW | STR | 1 | 17.6 | 0.03 | 0.06 | 0.01 | 105 | 116 | 123
110 | GRO | BVK | 1 | 4.91 | 0 | 0 | 0.05 | 195 | 201 | 220
110 | COL (I) | CDU | 1 | 2.66 | 0 | 0 | 0.02 | 143 | 143 | 143
110 | COL (N) | CPS | 1 | 46.7 | 0.06 | 0.16 | 0.02 | 82 | 95 | 103
110 | COL (I) | FIN (I) | 1 | 5.02 | 0 | 0.01 | 0.04 | 104 | 124 | 124
110 | COL (N) | LIM (N) | 1 | 18.63 | 0.02 | 0.06 | 0.01 | 82 | 95 | 103
110 | COL (N) | LOG | 1 | 8.1 | 0.01 | 0.03 | 0 | 82 | 95 | 103
110 | COL (N) | LOG | 2 | 8.1 | 0.01 | 0.03 | 0 | 82 | 95 | 103
110 | COL (N) | RSK | 1 | 20.01 | 0.02 | 0.07 | 0.01 | 186 | 191 | 193
110 | COO | FTT | 1 | 4.4 | 0 | 0.01 | 0.02 | 124 | 124 | 132
110 | COO | INC | 1 | 6.17 | 0.01 | 0.02 | 0.03 | 136 | 140 | 140
110 | COR | ENN (N) | 1 | 27.5 | 0.04 | 0.1 | 0.01 | 99 | 110 | 121
110 | COR | GWE | 1 | 10.9 | 0.01 | 0.04 | 0 | 178 | 197 | 210
110 | COS | ARI | 1 | 20.7 | 0.01 | 0.07 | 0.01 | 178 | 197 | 210
110 | COS | FLA | 1 | 3.4 | 0.01 | 0.01 | 0 | 99 | 110 | 121
110 | COS | FLA | 2 | 3.3 | 0.01 | 0.01 | 0 | 99 | 110 | 121
110 | COW | OLD | 1 | 2.3 | 0 | 0.01 | 0 | 105 | 116 | 123
110 | COW | OLD | 2 | 2.2 | 0 | 0.01 | 0 | 105 | 116 | 123
110 | COW | RAF | 1 | 6.9 | 0.01 | 0.02 | 0 | 99 | 110 | 121
110 | COW | WHI | 1 | 17.79 | 0.03 | 0.06 | 0.01 | 99 | 110 | 121
110 | CPK | CPK | 1 | 3.38 | 0 | 0 | 0.03 | 100 | 100 | 100
110 | CPK | TNY | 1 | 5.59 | 0 | 0.01 | 0.07 | 100 | 100 | 100
110 | CPS | KMT | 1 | 14.5 | 0.01 | 0.05 | 0.01 | 143 | 158 | 166
110 | CPS | LIM (N) | 1 | 29.5 | 0.04 | 0.1 | 0.01 | 82 | 95 | 103
110 | CPS | LMR | 1 | 9 | 0.01 | 0.03 | 0 | 82 | 95 | 103
110 | CPS | LMR | 2 | 9 | 0.01 | 0.03 | 0 | 82 | 95 | 103
110 | CPS | STR (N) | 1 | 27 | 0.02 | 0.05 | 0.02 | 109 | 119 | 124
110 | CPS | SPR | 1 | 9.23 | 0.01 | 0.03 | 0.01 | 82 | 95 | 103
110 | CPS | SPR | 2 | 9.38 | 0.01 | 0.03 | 0.01 | 82 | 95 | 103
110 | CRA | LWD | 1 | 6.69 | 0 | 0.02 | 0 | 178 | 197 | 210
110 | CRA | WEX | 1 | 22.82 | 0.02 | 0.08 | 0.01 | 99 | 110 | 113
110 | CRG | KEL | 1 | 23.1 | 0.03 | 0.08 | 0.01 | 82 | 95 | 103
110 | CRG | TMN | 1 | 36.24 | 0.05 | 0.12 | 0.02 | 109 | 114 | 124
110 | CRM | KLM | 1 | 1.35 | 0 | 0 | 0.01 | 140 | 140 | 140
110 | CRM | KLM | 2 | 1.35 | 0 | 0 | 0.01 | 140 | 140 | 140
110 | CRO | IA | 1 | 2.74 | 0 | 0.01 | 0 | 196 | 216 | 217
110 | CRO | KBY | 1 | 14.35 | 0.02 | 0.05 | 0.02 | 178 | 194 | 200
110 | CSH | CLN | 1 | 22.8 | 0.01 | 0.07 | 0.01 | 178 | 197 | 210
110 | CSH | DLT | 1 | 60.76 | 0.07 | 0.21 | 0.02 | 99 | 110 | 121
110 | CSH | ENN | 1 | 53.47 | 0.03 | 0.17 | 0.02 | 178 | 197 | 210
110 | CSH | GAL | 1 | 13.8 | 0.02 | 0.05 | 0 | 99 | 110 | 121
110 | CSH | GAL | 2 | 11.3 | 0.02 | 0.04 | 0 | 99 | 110 | 121
110 | CSH | GAL | 3 | 11.3 | 0.02 | 0.04 | 0 | 99 | 110 | 121
110 | CSH | SAL | 1 | 24.85 | 0.02 | 0.07 | 0.07 | 97 | 97 | 97
110 | CSH | SOM | 1 | 50.02 | 0.08 | 0.17 | 0.02 | 99 | 110 | 121
110 | CTN | TIP | 1 | 13.15 | 0.01 | 0.04 | 0.01 | 178 | 197 | 210
110 | CTY | FTT | 1 | 1.5 | 0 | 0 | 0.02 | 124 | 124 | 132
110 | CTY | INC | 1 | 8.9 | 0.01 | 0.03 | 0 | 103 | 116 | 123
110 | CUL | DGN | 1 | 34.24 | 0.02 | 0.11 | 0.02 | 178 | 192 | 192
110 | CUL | WAT | 1 | 13.14 | 0.01 | 0.03 | 0.06 | 178 | 194 | 200
110 | CUN | GLR | 1 | 26.29 | 0.04 | 0.09 | 0.01 | 178 | 194 | 209
110 | CUN | SLI | 1 | 21.1 | 0.03 | 0.07 | 0.01 | 178 | 194 | 209
110 | CUR | BKM | 1 | 17.3 | 0 | 0.02 | 0.19 | 190 | 190 | 190
110 | CUR | NEN | 1 | 18.83 | 0.03 | 0.07 | 0.01 | 105 | 116 | 123
110 | CUS | MLC | 1 | 13.67 | 0.02 | 0.05 | 0.01 | 136 | 150 | 159
110 | CUS | NEW (I) | 1 | 24.61 | 0.03 | 0.08 | 0.01 | 134 | 147 | 152
110 | CUS | PLS | 1 | 42.14 | 0.04 | 0.14 | 0.01 | 136 | 150 | 159
110 | CVW | COW | 1 | 17.22 | 0.02 | 0.05 | 0.02 | 99 | 110 | 121
110 | CVW | DKL | 1 | 0.36 | 0 | 0 | 0 | 105 | 116 | 123
110 | CVW | KRA | 1 | 7.59 | 0.01 | 0.03 | 0 | 99 | 110 | 121
110 | DAL | DAL | 1 | 12.2 | 0.02 | 0.04 | 0 | 105 | 116 | 123
110 | DDK | LOU | 1 | 16.81 | 0.03 | 0.06 | 0.01 | 99 | 110 | 121
110 | DDK | MLN | 1 | 7.5 | 0.01 | 0.03 | 0 | 99 | 110 | 121
110 | DER | KIN | 1 | 15.11 | 0.01 | 0.05 | 0.01 | 99 | 110 | 121
110 | DER | MAY | 1 | 43.45 | 0.03 | 0.15 | 0.02 | 74 | 84 | 93
110 | DER | TSB | 1 | 19.67 | 0.03 | 0.07 | 0.01 | 99 | 110 | 121
110 | DEY | DAL | 1 | 6.35 | 0 | 0.02 | 0 | 178 | 197 | 210
110 | DEY | PLS | 1 | 48.45 | 0.03 | 0.16 | 0.02 | 178 | 197 | 210
110 | DGN | WHE | 1 | 8.65 | 0.01 | 0.03 | 0 | 178 | 197 | 210
110 | DMY | CDN | 1 | 10.88 | 0.02 | 0.04 | 0 | 211 | 216 | 217
110 | DMY | MAC | 1 | 26.22 | 0.04 | 0.09 | 0.01 | 196 | 213 | 217
110 | DON | FIN (N) | 1 | 3.67 | 0 | 0.01 | 0.01 | 69 | 81 | 86
110 | DON | FIN (N) | 2 | 3.74 | 0 | 0.01 | 0.01 | 69 | 80 | 86
110 | DON | HAN | 1 | 6.07 | 0 | 0.01 | 0.14 | 144 | 144 | 158
110 | DON | HAN | 2 | 5.89 | 0 | 0.01 | 0.14 | 144 | 144 | 158
110 | DRM | CLO | 1 | 27 | 0.04 | 0.09 | 0.02 | 103 | 116 | 123
110 | DRM | LET | 1 | 8.35 | 0.01 | 0.03 | 0 | 99 | 110 | 123
110 | DRM | MEE | 1 | 5 | 0.01 | 0.02 | 0 | 99 | 110 | 121
110 | DRO | EKN | 1 | 24.59 | 0.03 | 0.07 | 0.01 | 82 | 95 | 103
110 | DRO | EKN | 2 | 24.59 | 0.03 | 0.07 | 0.01 | 82 | 95 | 103
110 | DRO | OMA | 1 | 9.23 | 0.02 | 0.05 | 0.01 | 82 | 95 | 103
110 | DRO | OMA | 2 | 9.23 | 0.02 | 0.05 | 0.01 | 82 | 95 | 103
110 | DRU | ENN | 1 | 17.44 | 0.03 | 0.06 | 0.01 | 99 | 110 | 121
110 | DRU (N) | TAN | 1 | 4.4 | 0 | 0.01 | 0 | 79 | 96 | 113
110 | DRU (N) | TAN | 2 | 4.4 | 0 | 0.01 | 0 | 79 | 96 | 113
110 | DRU (N) | TAN | 3 | 4.1 | 0.01 | 0.01 | 0 | 108 | 119 | 126
110 | DRU (N) | TMN | 1 | 22.69 | 0.03 | 0.08 | 0.01 | 109 | 119 | 124
110 | DRU (N) | TMN | 2 | 21.53 | 0.03 | 0.07 | 0.01 | 109 | 119 | 124
110 | DRY | GOR | 1 | 19.39 | 0.03 | 0.07 | 0.01 | 99 | 110 | 121
110 | DRY | LOU | 1 | 31.9 | 0.02 | 0.1 | 0.01 | 99 | 110 | 121
110 | DRY | PLA | 1 | 5.3 | 0.01 | 0.02 | 0 | 99 | 110 | 121
110 | DTN | FIN (I) | 1 | 9.25 | 0 | 0.01 | 0.11 | 140 | 140 | 140
110 | DTN | KLM | 1 | 3.2 | 0 | 0.01 | 0.03 | 140 | 140 | 140
110 | DUN | OMA | 1 | 36.1 | 0.04 | 0.12 | 0.01 | 186 | 191 | 193
110 | DUN | TMN | 1 | 6.53 | 0 | 0.02 | 0.01 | 157 | 171 | 178
110 | DUN | TMN | 2 | 5.82 | 0.01 | 0.02 | 0 | 144 | 144 | 144
110 | DUN | TMN | 3 | 6.01 | 0 | 0.02 | 0.02 | 186 | 191 | 193
110 | ENN (I) | SLC | 1 | 31 | 0 | 0.05 | 0.27 | 195 | 201 | 220
110 | FAS | FAS | 1 | 5 | 0.01 | 0.02 | 0 | 105 | 116 | 123
110 | FIN | GLA | 1 | 14.02 | 0.02 | 0.05 | 0.01 | 105 | 116 | 123
110 | FIN | GRA | 1 | 13.2 | 0.01 | 0.01 | 0.24 | 119 | 119 | 119
110 | FIN (N) | HAN | 1 | 3.03 | 0 | 0 | 0.02 | 144 | 144 | 144
110 | FIN (N) | HAN | 2 | 3.21 | 0 | 0 | 0.02 | 144 | 144 | 144
110 | FIN | MCD | 1 | 7.9 | 0 | 0.01 | 0.14 | 119 | 119 | 119
110 | FIN | POP | 1 | 4.3 | 0 | 0.01 | 0.03 | 120 | 120 | 131
110 | FIN | PTN | 1 | 3.52 | 0 | 0.01 | 0.01 | 80 | 105 | 119
110 | FIN | SVN | 1 | 32.22 | 0.04 | 0.1 | 0.06 | 105 | 115 | 115
110 | FLA | GIL | 1 | 10.6 | 0.02 | 0.04 | 0 | 105 | 116 | 123
110 | FLA | SLB | 1 | 21.7 | 0.03 | 0.08 | 0.01 | 99 | 110 | 123
110 | FLA | SLI | 1 | 50.5 | 0.08 | 0.17 | 0.02 | 99 | 110 | 121
110 | FLA | TON | 1 | 32.31 | 0.05 | 0.11 | 0.01 | 98 | 111 | 126
110 | FRA | HAR | 1 | 2.28 | 0 | 0 | 0.03 | 107 | 107 | 107
110 | FRA | HEU | 1 | 2.4 | 0 | 0 | 0.02 | 140 | 140 | 140
110 | FRA | INC | 1 | 5.6 | 0 | 0.01 | 0.07 | 107 | 107 | 107
110 | FRA | TRN | 1 | 2.8 | 0 | 0 | 0.03 | 140 | 140 | 140
110 | GAL | SEE | 1 | 25.53 | 0.01 | 0.03 | 0.14 | 99 | 110 | 121
110 | GAL | SAL | 1 | 6.12 | 0 | 0 | 0.07 | 99 | 106 | 106
110 | GCA | GRI | 1 | 8.87 | 0.01 | 0.03 | 0.01 | 103 | 120 | 131
110 | GCA | INC | 1 | 8.1 | 0.01 | 0.03 | 0.01 | 103 | 123 | 134
110 | GCA | INC | 2 | 8.1 | 0.01 | 0.03 | 0.01 | 103 | 123 | 134
110 | GCA | KUD | 2 | 2.1 | 0 | 0 | 0.02 | 140 | 140 | 140
110 | GCA | NAN | 1 | 1.82 | 0 | 0 | 0.01 | 120 | 120 | 131
110 | GCA | NAN | 2 | 1.74 | 0 | 0 | 0.01 | 120 | 120 | 131
110 | GI | KKY | 1 | 49.2 | 0.08 | 0.17 | 0.02 | 99 | 110 | 121
110 | GI | WAT | 1 | 11.7 | 0.01 | 0.04 | 0 | 178 | 197 | 210
110 | GI | WAT | 2 | 12.92 | 0.01 | 0.04 | 0.01 | 178 | 197 | 210
110 | GI | WEX | 1 | 34.5 | 0.02 | 0.11 | 0.01 | 178 | 197 | 210
110 | GLA | SVN | 1 | 18 | 0.02 | 0.06 | 0.05 | 136 | 150 | 154
110 | GLE (N) | KEL | 1 | 21.4 | 0.03 | 0.07 | 0.03 | 82 | 82 | 90
110 | GLE (N) | KEL | 2 | 21.4 | 0.03 | 0.07 | 0.03 | 82 | 82 | 90
110 | GLE | KCR | 1 | 11.32 | 0 | 0.01 | 0.12 | 122 | 122 | 122
110 | GOL | GL | 1 | 3.9 | 0.01 | 0.01 | 0 | 105 | 116 | 123
110 | GOR | MTH | 1 | 26.39 | 0.03 | 0.09 | 0.01 | 99 | 110 | 121
110 | GOR | NAV | 1 | 5.33 | 0.01 | 0.02 | 0 | 99 | 110 | 121
110 | GOR | NAV | 2 | 6.3 | 0.01 | 0.02 | 0 | 99 | 110 | 121
110 | GOR | NAV | 3 | 5.49 | 0.01 | 0.02 | 0.01 | 99 | 110 | 121
110 | GOR | PLA | 1 | 19.74 | 0.03 | 0.07 | 0.01 | 99 | 110 | 121
110 | GRA | NBY | 1 | 5.05 | 0 | 0.01 | 0.09 | 119 | 119 | 119
110 | GRI | GRI | 1 | 1 | 0 | 0 | 0 | 105 | 116 | 123
110 | GRI | MAY | 1 | 2.2 | 0 | 0.01 | 0 | 105 | 116 | 123
110 | GOR (N) | OMA | 1 | 17.12 | 0.01 | 0.07 | 0.01 | 200 | 200 | 200
110 | GOR (N) | TMN | 1 | 34.83 | 0.02 | 0.13 | 0.01 | 200 | 200 | 200
110 | HAN | LIS (N) | 1 | 9.2 | 0.01 | 0.03 | 0.02 | 82 | 95 | 103
110 | HAN | LIS (N) | 2 | 9.2 | 0.01 | 0.03 | 0.02 | 80 | 93 | 100
110 | HAR | RE | 1 | 5.63 | 0 | 0.01 | 0.07 | 107 | 107 | 107
110 | HEU | INC | 1 | 3.6 | 0 | 0.01 | 0.04 | 140 | 140 | 140
110 | IA | MAC | 1 | 18.16 | 0.03 | 0.06 | 0.01 | 196 | 213 | 217
110 | IKE | IKE | 1 | 0.15 | 0 | 0 | 0 | 80 | 105 | 119
110 | INC | MIL | 1 | 8.4 | 0 | 0.01 | 0.05 | 120 | 120 | 131
110 | KBY | KRA | 1 | 11.9 | 0.01 | 0.04 | 0 | 178 | 197 | 210
110 | KBY | KRA | 2 | 12.5 | 0.02 | 0.04 | 0 | 99 | 110 | 121
110 | KBY | MAL | 1 | 29.2 | 0.02 | 0.1 | 0.01 | 134 | 147 | 159
110 | KBY | MR | 1 | 4.44 | 0 | 0.02 | 0 | 103 | 119 | 130
110 | KBY | MR | 2 | 4.65 | 0.01 | 0.02 | 0 | 103 | 119 | 130
110 | KEL | RSK | 1 | 25.9 | 0.04 | 0.13 | 0.01 | 185 | 190 | 193
110 | KER | OUG | 1 | 22.6 | 0.01 | 0.07 | 0.01 | 178 | 197 | 210
110 | KMT | STR (N) | 1 | 11.2 | 0.01 | 0.04 | 0 | 143 | 158 | 166
110 | KMT | SLK | 1 | 6.2 | 0.01 | 0.02 | 0.01 | 109 | 119 | 124
110 | KIN | DFR | 1 | 29.25 | 0.02 | 0.1 | 0.01 | 99 | 110 | 121
110 | KIN | MUL | 1 | 24.92 | 0.02 | 0.08 | 0.02 | 178 | 197 | 210
110 | KHL | THU | 1 | 21.24 | 0.01 | 0.07 | 0.01 | 178 | 197 | 210
110 | KLM | NBY | 1 | 1.2 | 0 | 0 | 0.02 | 119 | 119 | 119
110 | KLM | POP | 1 | 6 | 0 | 0.01 | 0.04 | 120 | 120 | 131
110 | KLN | CUR | 1 | 14.77 | 0.01 | 0.05 | 0.01 | 136 | 150 | 159
110 | KLN | LIM (I) | 1 | 9 | 0.01 | 0.03 | 0 | 99 | 110 | 121
110 | KLN | LIM (I) | 2 | 11.7 | 0.02 | 0.04 | 0.01 | 80 | 95 | 110
110 | KLN | SNG | 1 | 4.05 | 0 | 0.01 | 0 | 178 | 194 | 209
110 | KPG | CNG | 1 | 0.3 | 0 | 0 | 0 | 140 | 140 | 140
110 | KPG | KNR | 1 | 14.95 | 0.02 | 0.05 | 0.01 | 136 | 150 | 159
110 | KPG | RAT (I) | 1 | 32.42 | 0.03 | 0.11 | 0.02 | 136 | 150 | 159
110 | KPG | TB | 1 | 1.61 | 0 | 0.01 | 0 | 99 | 110 | 121
110 | KPG | TB | 2 | 1.61 | 0 | 0.01 | 0 | 99 | 110 | 121
110 | KPG | TRL | 1 | 39.38 | 0.06 | 0.14 | 0.01 | 99 | 110 | 121
110 | KPG | TRL | 2 | 43.58 | 0.03 | 0.14 | 0.02 | 178 | 190 | 190
110 | KLS | KKY | 1 | 34.3 | 0.05 | 0.12 | 0.01 | 99 | 110 | 121
110 | KNR | TRI | 1 | 4.29 | 0 | 0.01 | 0.01 | 178 | 194 | 209
110 | KNR | TRI | 2 | 4.21 | 0 | 0.01 | 0 | 99 | 110 | 121
110 | KRA | BAR | 1 | 19.45 | 0.02 | 0.07 | 0.01 | 136 | 150 | 159
110 | KRA | MID | 1 | 10.7 | 0.02 | 0.04 | 0 | 99 | 110 | 121
110 | KRA | WHO | 1 | 41.46 | 0.03 | 0.14 | 0.02 | 178 | 197 | 210
110 | KTL | MAY | 1 | 21.39 | 0.02 | 0.07 | 0.01 | 99 | 110 | 121
110 | KTL | MON | 1 | 8.88 | 0.01 | 0.03 | 0 | 136 | 150 | 159
110 | KTN | WAT | 1 | 3.3 | 0 | 0 | 0.04 | 99 | 110 | 121
110 | KUR | NAV | 1 | 6.1 | 0.01 | 0.02 | 0 | 99 | 110 | 123
110 | LA | MUL | 1 | 46.27 | 0.07 | 0.16 | 0.02 | 99 | 110 | 121
110 | LA | RIC | 1 | 15.74 | 0.02 | 0.05 | 0.01 | 99 | 110 | 123
110 | LA | RIC | 2 | 12.55 | 0.02 | 0.04 | 0.01 | 99 | 110 | 123
110 | LA | SLB | 1 | 9.1 | 0.01 | 0.03 | 0 | 99 | 110 | 123
110 | LET | GL | 1 | 38.4 | 0.06 | 0.13 | 0.01 | 99 | 110 | 121
110 | LET | STR (N) | 1 | 22.25 | 0.04 | 0.08 | 0.01 | 99 | 110 | 123
110 | LET | TIV | 1 | 45.2 | 0.05 | 0.15 | 0.02 | 136 | 150 | 159
110 | LET | TLK | 1 | 34.05 | 0.05 | 0.12 | 0.01 | 105 | 116 | 123
110 | LIB | MR | 1 | 2.7 | 0 | 0 | 0.02 | 100 | 100 | 100
110 | LIB | MR | 2 | 2.74 | 0 | 0 | 0.02 | 99 | 110 | 119
110 | LIM (I) | MTN | 1 | 6.47 | 0.01 | 0.02 | 0 | 178 | 197 | 210
110 | LIM (I) | RAT | 1 | 28.35 | 0.04 | 0.1 | 0.01 | 99 | 110 | 121
110 | LIS | LOU | 1 | 40.4 | 0.06 | 0.14 | 0.01 | 99 | 110 | 123
110 | LIS | SKL | 1 | 39.3 | 0.06 | 0.14 | 0.01 | 99 | 110 | 123
110 | LIS (N) | TAN | 1 | 31 | 0.04 | 0.11 | 0.01 | 82 | 95 | 103
110 | LIS (N) | TAN | 2 | 29.2 | 0.03 | 0.1 | 0.01 | 80 | 93 | 100
110 | LOU | MLN | 1 | 13 | 0.02 | 0.05 | 0 | 99 | 110 | 121
110 | LOU | MTH | 1 | 15.1 | 0.02 | 0.05 | 0.01 | 99 | 110 | 121
110 | LOU | RRU | 1 | 38.82 | 0.06 | 0.13 | 0.01 | 95 | 103 | 112
110 | LSN | THU | 1 | 10.4 | 0.02 | 0.04 | 0 | 104 | 113 | 122
110 | MKL | OMA | 1 | 37.5 | 0.03 | 0.11 | 0.02 | 139 | 150 | 157
110 | MAY | BLK | 1 | 30.9 | 0.03 | 0.1 | 0.01 | 99 | 110 | 121
110 | MAY | GRI | 1 | 2.2 | 0 | 0.01 | 0 | 99 | 110 | 120
110 | MAY | RNW | 1 | 7.1 | 0.01 | 0.02 | 0 | 80 | 92 | 103
110 | MAY | RYB | 1 | 9.02 | 0.01 | 0.03 | 0.01 | 178 | 197 | 219
110 | MCD | NQS | 1 | 2 | 0 | 0 | 0.04 | 119 | 119 | 119
110 | MCD | WOL | 1 | 1.4 | 0 | 0 | 0.01 | 120 | 120 | 131
110 | MHL | RE | 1 | 3 | 0 | 0 | 0.03 | 140 | 140 | 140
110 | MHL | TRN | 1 | 1.4 | 0 | 0 | 0.01 | 140 | 140 | 140
110 | MID | WHI | 1 | 20.02 | 0.03 | 0.07 | 0.01 | 99 | 110 | 121
110 | MIL | RE | 1 | 4.9 | 0 | 0.01 | 0.08 | 100 | 100 | 100
110 | MIL | RE | 2 | 5.55 | 0 | 0.01 | 0.03 | 120 | 120 | 131
110 | MIL | TNY | 1 | 5.55 | 0 | 0.01 | 0.07 | 100 | 100 | 100
110 | MLC | TSB | 1 | 18.29 | 0.02 | 0.06 | 0.03 | 135 | 147 | 159
110 | MOY | TAW | 1 | 8.39 | 0.01 | 0.03 | 0 | 99 | 110 | 123
110 | MOY | TAW | 2 | 8.3 | 0.01 | 0.03 | 0 | 99 | 110 | 121
110 | MP | TBK | 1 | 7.29 | 0.01 | 0.02 | 0 | 178 | 197 | 210
110 | MR | TBG | 1 | 3.25 | 0 | 0 | 0.04 | 178 | 198 | 219
110 | MR | TBG | 2 | 2.8 | 0 | 0 | 0.03 | 178 | 206 | 219
110 | MTN | MUN | 1 | 0.7 | 0 | 0 | 0 | 105 | 116 | 123
110 | MTN | MUN | 2 | 0.7 | 0 | 0 | 0 | 105 | 116 | 123
110 | NEW (I) | BLK | 1 | 12.2 | 0.01 | 0.04 | 0 | 136 | 150 | 159
110 | NEW (N) | TAN | 1 | 24.1 | 0.03 | 0.08 | 0.01 | 82 | 95 | 103
110 | NEW (N) | TAN | 2 | 24 | 0.03 | 0.08 | 0.01 | 82 | 95 | 103
110 | NQS | RE | 1 | 2.1 | 0 | 0 | 0.04 | 119 | 119 | 119
110 | OMA | STR (N) | 1 | 35.5 | 0.05 | 0.12 | 0.01 | 109 | 119 | 124
110 | OMA | STR (N) | 2 | 35.5 | 0.05 | 0.13 | 0.01 | 82 | 95 | 103
110 | OMA | TRE | 1 | 21.45 | 0.03 | 0.07 | 0.01 | 186 | 191 | 193
110 | GLR | MOY | 1 | 13.96 | 0.02 | 0.05 | 0 | 105 | 116 | 123
110 | OUG | OUG | 1 | 11 | 0.02 | 0.04 | 0 | 105 | 116 | 123
110 | PA | STR | 1 | 22.4 | 0.04 | 0.08 | 0.01 | 105 | 116 | 123
110 | PB | RE | 3 | 1.4 | 0 | 0 | 0.05 | 269 | 269 | 269
110 | PB | RE | 4 | 1.4 | 0 | 0 | 0.05 | 269 | 269 | 269
110 | RAF | RSY | 1 | 2.1 | 0 | 0.01 | 0 | 63 | 82 | 92
110 | RAF | TBG | 1 | 11.03 | 0.02 | 0.04 | 0.01 | 195 | 201 | 2200
110 | RAF | TBG | 2 | 9.5 | 0.01 | 0.03 | 0.01 | 178 | 194 | 209
110 | RE | WBK | 1 | 0.62 | 0 | 0 | 0.02 | 125 | 130 | 141
110 | REM | TRL | 1 | 11.99 | 0.01 | 0 | 0.11 | 125 | 130 | 141
110 | RNW | DFR | 1 | 25.9 | 0.02 | 0.09 | 0.01 | 99 | 110 | 121
110 | RRU | SKL | 1 | 12.67 | 0.02 | 0.04 | 0 | 95 | 103 | 112
110 | KNY | KLH | 1 | 11.7 | 0 | 0.02 | 0.11 | 190 | 190 | 190
110 | KNY | SCR | 1 | 33.33 | 0.03 | 0.11 | 0.04 | 135 | 147 | 159
110 | KNY | SHL | 1 | 22.71 | 0.02 | 0.06 | 0.08 | 195 | 201 | 220
110 | KNY | UGL | 1 | 3.42 | 0 | 0 | 0.04 | 195 | 201 | 220
110 | BRA | NEW (I) | 1 | 22.7 | 0.02 | 0.08 | 0.01 | 136 | 150 | 159
110 | BRA | PLS | 1 | 19.26 | 0.03 | 0.07 | 0.01 | 99 | 110 | 121
110 | SH | DAL | 1 | 12 | 0.01 | 0.04 | 0.01 | 178 | 197 | 210
110 | SH | IKE | 1 | 53.94 | 0.03 | 0.18 | 0.02 | 178 | 197 | 210
110 | SH | SOM | 1 | 13.8 | 0.02 | 0.05 | 0.01 | 105 | 116 | 123
110 | SLI | SRA | 1 | 11.1 | 0.02 | 0.04 | 0 | 99 | 110 | 121
110 | SLI | SRA | 2 | 12 | 0.02 | 0.04 | 0 | 99 | 110 | 121
110 | SBH | MCE | 1 | 4.72 | 0.01 | 0.02 | 0.01 | 99 | 110 | 121
110 | SOM | SOM | 1 | 2 | 0 | 0.01 | 0 | 105 | 116 | 123
110 | SOR | TLK | 1 | 4.4 | 0.01 | 0.02 | 0 | 105 | 116 | 123
110 | STR | STR | 1 | 2 | 0 | 0.01 | 0 | 105 | 116 | 123
110 | TAN | WAR | 1 | 12.9 | 0.01 | 0.04 | 0.01 | 79 | 96 | 113
110 | TAN | WAR | 2 | 12.9 | 0.01 | 0.04 | 0.01 | 79 | 96 | 113
110 | TBK | TBK | 1 | 2.9 | 0.01 | 0.01 | 0 | 105 | 116 | 123
110 | THU | IKE | 1 | 25.68 | 0.02 | 0.08 | 0.01 | 178 | 197 | 210
110 | TRE | TMN | 1 | 42.93 | 0.03 | 0.08 | 0.03 | 186 | 191 | 193
110 | TRL | OUG | 1 | 11.3 | 0.01 | 0.04 | 0 | 178 | 197 | 210
110 | WHE | WHE | 1 | 1.5 | 0 | 0 | 0.02 | 124 | 124 | 124
220 | BTN | CLE | 2 | 2.5 | 0.0001 | 0.0004 | 0.083 | 570 | 570 | 570
220 | CDU | CRH | 2 |  | 4.8e-05 | 0.00018 | 0.0415 | 570 | 570 | 570
220 | CDU | CRH | 1 |  | 4.8e-05 | 0.00018 | 0.0415 | 570 | 570 | 570
220 | BRT | CLE | 1 | 2.5 | 0.0001 | 0.0004 | 0.083 | 570 | 570 | 570
110 | KUD | CBT | 1 | 0.75 | 0.0002 | 0.0009 | 0.0083 | 187 | 187 | 223
110 | DTN | BLC | 2 | 8 | 0.0041 | 0.00893 | 0.04864 | 140 | 140 | 143
110 | CKG | CBT | 2 | 0.75 | 0.0002 | 0.0009 | 0.0083 | 187 | 187 | 223
110 | GCA | INC | 3 | 7.71 | 0.0047 | 0.0044 | 0.0939 | 124 | 124 | 124
110 | GCA | KUD | 2 | 2.1 | 0.0015 | 0.0032 | 0.0211 | 140 | 140 | 140
110 | ADM | GCA | 1 | 2.5 | 0.0018 | 0.0038 | 0.0251 | 140 | 140 | 140
110 | KIN | DFR | 1 | 29.25 | 0.0213 | 0.0957 | 0.0103 | 99 | 99 | 121
110 | KNY | BUF | 1 | 0.5 | 0.0002 | 0.0007 | 0.0056 | 140 | 140 | 140
110 | KPG | TRL | 2 | 43.578 | 0.0271 | 0.1405 | 0.0231 | 178 | 178 | 190
110 | LIS | LIS | 1 | 0.25 | 0.0001 | 0.0003 | 0.0028 | 187 | 187 | 223
110 | BKY | CKG | 1 | 3 | 0.0007 | 0.0033 | 0.033 | 187 | 187 | 223
110 | BNK | INC | 1 | 10 | 0.0023 | 0.011 | 0.11 | 187 | 187 | 223
110 | BNK | CBT | 1 | 1 | 0.0003 | 0.0011 | 0.011 | 187 | 187 | 223
110 | BKY | CBT | 2 | 0.6 | 0.0003 | 0.0011 | 0.011 | 187 | 187 | 223
110 | SXH | SOM | 1 | 45.45 | 0.0707 | 0.1563 | 0.0146 | 105 | 105 | 123
110 | KRA | KRA | 1 |  | 0 | 0.0001 | 0 | 178 | 178 | 210
110 | BOG | CRA | 1 | 24.677 | 0.0179 | 0.0811 | 0.0087 | 178 | 178 | 210
110 | ADM | KUD | 1 |  | 0.00075 | 0.0016 | 0.01055 | 140 | 140 | 140
110 | BLE | KPG | 1 | 28.23 | 0.0178 | 0.0917 | 0.01 | 178 | 178 | 210
110 | AUG | BLE | 1 | 4.56 | 0.0029 | 0.0149 | 0.0017 | 178 | 178 | 210
110 | AUG | KPG | 1 | 32.83 | 0.0207 | 0.1067 | 0.0116 | 178 | 178 | 210
110 | BLU | CDU | 1 | 18.33 | 0.0168 | 0.0557 | 0.0308 | 130 | 130 | 130
110 | BLU | MUL | 1 | 56.18 | 0.079 | 0.1906 | 0.025 | 105 | 105 | 123
110 | DJG | TRL | 1 | 32.333 | 0.0203 | 0.1047 | 0.0138 | 178 | 178 | 210
110 | BLC | KLM | 1 | 4 | 0.0023 | 0.005 | 0.0291 | 140 | 140 | 140
110 | DJG | KPG | 1 | 13.895 | 0.0081 | 0.0452 | 0.0104 | 178 | 178 | 210
110 | BOG | TTU | 1 | 11.15 | 0.007 | 0.0362 | 0.0045 | 178 | 178 | 210
110 | CSH | SXH | 1 | 4.65 | 0.0073 | 0.016 | 0.0015 | 105 | 105 | 123
110 | CSH | SOM | 1 | 50.019 | 0.0778 | 0.172 | 0.0161 | 99 | 99 | 121
110 | CRA | TTU | 1 | 13.653 | 0.011 | 0.0452 | 0.0054 | 178 | 178 | 210
110 | CDU | MUL | 1 | 73.255 | 0.09326 | 0.24155 | 0.03764 | 104 | 104 | 122
110 | KRA | MEN | 1 | 2.8 | 0.0017 | 0.0016 | 0.0341 | 124 | 124 | 124
110 | BLC | GRA | 1 | 4.3 | 0.0025 | 0.0053 | 0.0309 | 140 | 140 | 140
400 | KPG | MP | 1 | 6 | 0.00084 | 0.00023 | 0.54891 | 1210 | 1210 | 1210
220 | ORL | ORL | 1 | 20.1 | 0.0007 | 0.0079 | 0.5502 | 593 | 593 | 593
220 | KYT | WOO | 1 | 13.8 | 0.003 | 0.0109 | 0.1124 | 761 | 761 | 746
220 | KYT | MAY | 1 | 13.5 | 0.003 | 0.0106 | 0.112 | 761 | 761 | 746
220 | LOU | WOO | 1 | 61.2 | 0.0071 | 0.053 | 0.08 | 350 | 350 | 436
220 | LOU | ORL | 1 | 14.5 | 0.0017 | 0.0126 | 0.019 | 434 | 434 | 513
220 | WOO | ORL | 1 | 49.2 | 0.0058 | 0.0427 | 0.0644 | 434 | 434 | 513
220 | ORL | ORL | 1 | 15.9 | 0.0007 | 0.0023 | 0.5279 | 570 | 570 | 570
220 | FIN | SHL | 1 | 13.4 | 0.0005 | 0.0053 | 0.3668 | 536 | 536 | 557
220 | MAY | WOO | 1 | 22.3 | 0.0027 | 0.0195 | 0.0295 | 350 | 350 | 436
220 | BLC | SHL | 1 | 23.4 | 0.001 | 0.0034 | 0.7769 | 570 | 570 | 570
110 | INC | YMW | 1 | 3.18 | 0.0008 | 0.0035 | 0.035 | 187 | 187 | 223
110 | BAL | DEE | 1 | 10.75 | 0.0068 | 0.0349 | 0.0044 | 178 | 178 | 210
110 | BAL | DRY | 1 | 20 | 0.0126 | 0.065 | 0.0071 | 178 | 178 | 210
110 | BAG | CLG | 1 | 0.85 | 0.0002 | 0.001 | 0.0094 | 192 | 192 | 192
110 | BRO | RSK | 1 |  | 0.01 | 0.062 | 0.02 | 144 | 144 | 144
110 | GRV | RSK | 1 |  | 0.0098 | 0.059 | 0.0167 | 187 | 187 | 200
110 | BAG | SBH | 1 | 1.2 | 0.0003 | 0.0014 | 0.0133 | 192 | 192 | 192
110 | CLG | FIN | 1 | 3.64 | 0.0035 | 0.0111 | 0.0073 | 124 | 124 | 124
110 | HRR | KIN | 1 | 5.825 | 0.006 | 0.0193 | 0.0034 | 136 | 136 | 159
110 | GCA | YMW | 1 | 5.09 | 0.0012 | 0.0056 | 0.056 | 187 | 187 | 223
110 | GOR | GOR | 1 | 0.5 | 0.0002 | 0.0006 | 0.0056 | 187 | 187 | 223
110 | GLN | PLA | 1 | 26.55 | 0.0167 | 0.0863 | 0.0094 | 178 | 178 | 210
110 | HRR | DFR | 1 | 9.414 | 0.0064 | 0.0307 | 0.0034 | 104 | 104 | 157
110 | GI | ROP | 1 | 19.7 | 0.0123 | 0.0635 | 0.0103 | 178 | 178 | 210
110 | CKN | CUS | 1 | 0.5 | 0.0002 | 0.0007 | 0.0056 | 140 | 140 | 140
110 | FIN | MCE | 1 | 8.37 | 0.0081 | 0.0262 | 0.0127 | 124 | 124 | 124
110 | KIN | MUL | 1 | 24.919 | 0.0155 | 0.07731 | 0.02271 | 178 | 178 | 210
110 | CFN | KIN | 1 | 6.59 | 0.0042 | 0.0215 | 0.0024 | 178 | 178 | 210
110 | CFN | MUL | 1 | 18.97 | 0.012 | 0.0617 | 0.0067 | 178 | 178 | 210
110 | CKG | KUD | 1 | 0.75 | 0.0002 | 0.0009 | 0.0083 | 187 | 187 | 223
110 | DRY | DEE | 1 | 9.55 | 0.006 | 0.031 | 0.004 | 178 | 178 | 210
110 | CDU | PLA | 1 | 37 | 0.0233 | 0.1202 | 0.0131 | 178 | 178 | 210
110 | CDU | GLN | 1 | 11.05 | 0.007 | 0.0359 | 0.0039 | 178 | 178 | 210
110 | CLU | CBT | 1 | 0.1 | 0.0001 | 0.0002 | 0.0012 | 187 | 187 | 223
110 | CLU | KUD | 1 | 0.9 | 0.0003 | 0.001 | 0.01 | 187 | 187 | 223
110 | GI | WEX | 1 | 34.5 | 0.0217 | 0.1121 | 0.0122 | 178 | 178 | 210
110 | AGN | CBT | 2 | 0.2 | 0.0001 | 0.0003 | 0.0022 | 187 | 187 | 223
110 | SNU | MCE | 1 | 4.7271 | 0.0047 | 0.0151 | 0.0054 | 99 | 99 | 121
110 | BRO | AGI | 1 |  | 0.0027 | 0.0164 | 0.0047 | 144 | 144 | 144
110 | AGN | CBT | 1 | 0.2 | 0.0001 | 0.0003 | 0.0022 | 187 | 187 | 223
110 | ROP | WEX | 1 | 15.2 | 0.0095 | 0.0489 | 0.0087 | 178 | 178 | 210
110 | THU | THU | 1 | 0.001 | 0.0001 | 0.0001 | 0.0001 | 218 | 218 | 232
275 | TAN | TMN | 1 |  | 0.00116 | 0.01085 | 0.0647 | 710 | 710 | 881
275 | TMN | TUR | 1 |  | 0.00024 | 0.00227 | 0.01354 | 710 | 710 | 881
275 | TAN | TUR | 2 |  | 0.00092 | 0.00862 | 0.05139 | 710 | 710 | 881
275 | TAN | TMN | 2 |  | 0.00116 | 0.01085 | 0.0647 | 710 | 710 | 881
275 | TMN | TUR | 2 |  | 0.00024 | 0.00227 | 0.01354 | 710 | 710 | 881
275 | TAN | TUR | 1 |  | 0.00092 | 0.00862 | 0.05139 | 710 | 710 | 881
220 | GI | LWN | 1 | 0.4 | 0.0001 | 0.0002 | 0.011 | 593 | 593 | 593
110 | AGT | CLM | 1 | 8 | 0.0084 | 0.0223 | 0.0502 | 200 | 200 | 200
110 | PLA | OBE | 1 | 2.955 | 0.0043 | 0.0096 | 0.0038 | 105 | 105 | 123
110 | DGN | RTO | 1 | 15.475 | 0.0098 | 0.0502 | 0.006 | 178 | 178 | 210
110 | DRY | PLA | 1 | 5.3 | 0.0082 | 0.0182 | 0.0017 | 99 | 99 | 121
110 | DRY | OBE | 1 | 2.875 | 0.0042 | 0.0093 | 0.0038 | 105 | 105 | 123
110 | KLC | KLC | 1 |  | 0.005 | 0.0312 | 0.00298 | 126 | 126 | 156
110 | FGH | MOY | 1 | 15.87 | 0.0197 | 0.0472 | 0.048 | 105 | 105 | 123
110 | CRR | CRR | 1 | 2 | 0.00059 | 0.00224 | 0.0156 | 80 | 80 | 50
110 | CAS | FIN (N) | 1 | 9.1 | 0.01369 | 0.03189 | 0.003 | 70 | 70 | 87
110 | CUL | DGN | 1 | 34.239 | 0.0215 | 0.1093 | 0.0203 | 178 | 178 | 192
110 | DLN | SH | 1 | 3.5 | 0.0009 | 0.0043 | 0.0386 | 140 | 140 | 140
110 | CRR | PGN | 1 | 2.4 | 0.0017 | 0.00269 | 0.01872 | 60 | 60 | 60
110 | MAY | TEN | 1 | 18.71 | 0.0118 | 0.0605 | 0.0093 | 112 | 112 | 112
110 | CD | KLP | 1 | 32.091 | 0.0202 | 0.1043 | 0.0113 | 178 | 178 | 210
110 | CD | KBY | 1 | 32.338 | 0.01988 | 0.1043 | 0.02497 | 178 | 178 | 209
110 | GLE (N) | KEL | 1 |  | 0.02726 | 0.06833 | 0.02722 | 82 | 82 | 90
110 | KEL | KEL | 1 |  | 0.00033 | 0.00131 | 0.00798 | 144 | 144 | 144
110 | GLR | MOY | 1 | 13.956 | 0.0216 | 0.048 | 0.0045 | 105 | 105 | 123
110 | CLD | GCA | 2 | 2.02 | 0.0005 | 0.0025 | 0.0223 | 140 | 140 | 140
110 | CUL | RTO | 1 | 19.175 | 0.0121 | 0.0622 | 0.0074 | 178 | 178 | 210
110 | LET | LNA | 1 | 12.23 | 0.0128 | 0.0408 | 0.0042 | 136 | 136 | 159
110 | KBY | MAL | 1 | 29.2 | 0.0184 | 0.0949 | 0.0103 | 134 | 134 | 159
110 | KBY | MR | 1 | 4.438 | 0.00448 | 0.01466 | 0.004 | 103 | 103 | 130
110 | KBY | KRA | 2 | 12.5 | 0.0183 | 0.0428 | 0.0041 | 99 | 99 | 121
110 | TIV | MLG | 1 | 6.1 | 0.0044 | 0.0091 | 0.0612 | 140 | 140 | 140
110 | CAR | CAS | 1 |  | 0.03714 | 0.0875 | 0.00798 | 69 | 69 | 86
110 | CAR | CAS | 2 |  | 0.03695 | 0.08641 | 0.00803 | 70 | 70 | 87
110 | KLP | KRA | 2 | 12.5 | 0.0183 | 0.0428 | 0.0041 | 99 | 99 | 121
110 | GOR | PLA | 1 | 19.732 | 0.0302 | 0.0681 | 0.0064 | 99 | 99 | 121
110 | GOR | GRH | 1 | 14.125 | 0.0214 | 0.0484 | 0.0051 | 105 | 105 | 123
110 | DER | MAY | 1 | 43.448 | 0.0277 | 0.14567 | 0.0177 | 74 | 74 | 93
110 | AIR | ROS | 1 |  | 0.01312 | 0.03406 | 0.00338 | 82 | 82 | 103
110 | CLD | GCA | 1 | 1.87 | 0.0005 | 0.0023 | 0.0207 | 140 | 140 | 140
110 | DER | TEN | 1 | 25.125 | 0.0158 | 0.0817 | 0.0089 | 178 | 178 | 210
110 | CPS | CLM | 1 | 3.6 | 0.00101 | 0.0028 | 0.0867 | 200 | 200 | 200
110 | BGT | KKY | 1 | 22 | 0.0139 | 0.0715 | 0.0078 | 178 | 178 | 210
110 | CAS | FIN (N) | 1 | 9.1 | 0.01376 | 0.0323 | 0.003 | 69 | 69 | 86
110 | LNA | TIV | 1 | 33.13 | 0.0345 | 0.1106 | 0.0113 | 136 | 136 | 159
110 | FGH | GLR | 1 | 5.701 | 0.0038 | 0.0122 | 0.0448 | 105 | 105 | 123
110 | GRH | PLA | 1 | 6.05 | 0.0094 | 0.0208 | 0.0025 | 105 | 105 | 123
110 | LET | TIV | 1 | 45.2 | 0.0471 | 0.1508 | 0.0154 | 136 | 136 | 159
110 | KLP | MAL | 1 | 29.2 | 0.0184 | 0.0949 | 0.0103 | 134 | 134 | 159
220 | DSN | MAY | 2 | 30.55 | 0.0036 | 0.0265 | 0.04 | 434 | 434 | 513
220 | DSN | MAY | 2 | 30.55 | 0.0036 | 0.0265 | 0.04 | 350 | 350 | 436
110 | BDM | MID | 1 | 3.516 | 0.0047 | 0.0122 | 0.0012 | 99 | 99 | 121
110 | BDM | WHI | 1 | 18.306 | 0.0268 | 0.0628 | 0.006 | 99 | 99 | 121
110 | BGT | CNB | 1 | 28 | 0.0176 | 0.091 | 0.0099 | 178 | 178 | 210
110 | KEL | RSK | 2 | 25.903 | 0.02167 | 0.1344 | 0.0129 | 188 | 188 | 213
110 | ATY | PLS | 1 | 25.482 | 0.03822 | 0.08764 | 0.00848 | 99 | 99 | 121
110 | ARK | PHY | 2 | 2.38 | 0.0015 | 0.0078 | 0.0009 | 178 | 178 | 210
110 | MOY | TON | 1 | 58 | 0.0365 | 0.1884 | 0.0205 | 178 | 178 | 210
110 | MID | WHI | 1 | 20.022 | 0.0303 | 0.0691 | 0.0065 | 99 | 99 | 121
110 | ATY | CNB | 1 | 21.94 | 0.0138 | 0.0713 | 0.0078 | 178 | 178 | 210
110 | AGN | KSE | 1 | 1.7 | 0.0004 | 0.0019 | 0.0188 | 187 | 187 | 223
110 | ARK | PHY | 1 | 2.25 | 0.0015 | 0.0074 | 0.0008 | 178 | 178 | 210
110 | BKY | KCY | 1 | 0.75 | 0.0002 | 0.0009 | 0.0083 | 187 | 187 | 223
110 | GAR | GLN | 1 | 0.1 | 0.0001 | 0.0002 | 0.0012 | 140 | 140 | 140
110 | PHY | SHE | 1 | 0.375 | 0.0003 | 0.0013 | 0.0002 | 178 | 178 | 210
110 | ARK | SHE | 2 | 2.2 | 0.0035 | 0.0077 | 0.0008 | 34 | 34 | 57
110 | CNB | PLS | 1 | 8.36 | 0.0051 | 0.0261 | 0.0083 | 178 | 178 | 210
110 | CBT | KCY | 1 | 0.75 | 0.0002 | 0.0009 | 0.0083 | 187 | 187 | 223
110 | CBT | KSE | 1 | 1.9 | 0.0005 | 0.0021 | 0.021 | 187 | 187 | 223
400 | TUR | WOO | 1 |  | 0.0027 | 0.0311 | 0.7066 | 1424 | 1424 | 1731
400 | CNB | MP | 1 |  | 0.0033 | 0.01134 | 0.858 | 1577 | 1577 | 1944
400 | DSN | MP | 1 | 208.5 | 0.00405 | 0.04359 | 1.1397 | 1283 | 1283 | 1454
400 | CNB | DSN | 1 |  | 0.0009 | 0.003 | 0.226 | 1577 | 1577 | 1944
110 | CNB | CNB | 1 |  | 0 | 0.0001 | 0 | 178 | 178 | 210
110 | RSK | TGW | 1 |  | 0.01264 | 0.07231 | 0.03087 | 200 | 200 | 200
110 | KEL | TGW | 1 |  | 0.0097 | 0.04125 | 0.00443 | 200 | 200 | 200
110 | CRG | KEL | 1 |  | 0.02933 | 0.07667 | 0.01292 | 82 | 82 | 103
110 | CEN | CEN | 1 | 0.001 | 0.0001 | 0.0001 | 0.0001 | 187 | 187 | 223
110 | BNM | CEN | 1 |  | 0.00024 | 0.00093 | 0.00647 | 999 | 999 | 999
110 | CRG | TGW | 1 |  | 0.01276 | 0.034 | 0.00896 | 109 | 109 | 124
110 | GI | WAT | 2 | 12.901 | 0.0082 | 0.042 | 0.0046 | 178 | 178 | 210

## transformer
[8 empty] | Table B-4 Characteristics of Existing 3 Winding Transformers in Northern Ireland | [13 empty] | Table B-5 Characteristics of Existing 2 Winding Transformers in Northern Ireland
|  |  |  | Impedance on |  | Voltage Ratio Tapping Range |  |  |  | Impedance pu on 100 MVA base | [8 empty] | Off Nominal Ratio (pu) |  | No. of Taps |  |  | Rating (MVA) | Impedance pu on rating |  | Off nominal ratio
Station | Transformer | Rating (MVA) | HV/LV (kV) | 100 MVA Base (pu) |  |  |  | Substation/ Transformer | HV/LV (kV) | W1-2 |  | W2-3 |  | W3-1 |  | Rating (MVA) | [5 empty] | Station | HV/LV (kV) |  | base |  |  |  | No. of Taps
|  |  |  | R | X | + | - |  |  | R | X | R | X | R | X | W1 | W2 | W3 | Upper | Lower |  |  |  |  | R | X | Upper | Lower
DSN | T4201 | 500 | 400/220 | 0.0002 | 0.0317 | 0.013 | 0.156 | BPS IBTx 1 | 275/110 | 0.002 | 0.064 | 0.002 | 0.209 | 0 | 0.133 | 240 | 240 | 30 | 1.15 | 0.85 | 19 | AGH | 110/33 | 90 | 0.0039 | 0.2464 | 1.1 | 0.8 | 19
DSN | T4202 | 500 | 400/220 | 0.0003 | 0.027 | 0.105 | 0.079 | BPS IBTx 2 | 275/110 | 0.002 | 0.064 | 0.002 | 0.206 | 0 | 0.128 | 240 | 240 | 30 | 1.15 | 0.85 | 19 | ANT | 110/33 | 90 | 0.0039 | 0.2464 | 1.1 | 0.8 | 19
MP | T4201 | 500 | 400/220 | 0.0003 | 0.027 | 0.105 | 0.079 | CAS IBTx 1 | 275/110 | 0.001 | 0.064 | 0.001 | 0.224 | 0 | 0.145 | 240 | 240 | 30 | 1.15 | 0.85 | 19 | ANT | 110/33 | 90 | 0.0039 | 0.2473 | 1.1 | 0.8 | 19
MP | T4202 | 500 | 400/220 | 0.0002 | 0.0329 | 0.013 | 0.156 | CAS IBTx 2 | 275/110 | 0.002 | 0.064 | 0.002 | 0.209 | 0 | 0.133 | 240 | 240 | 30 | 1.15 | 0.85 | 19 | BMA | 110/33 | 90 | 0.0039 | 0.2447 | 1.1 | 0.8 | 19
OST | T4201 | 500 | 400/220 | 0.0003 | 0.027 | 0.105 | 0.079 | CAS IBTx 3 | 275/110 | 0.002 | 0.066 | 0.002 | 0.238 | 0 | 0.159 | 240 | 240 | 30 | 1.15 | 0.85 | 19 | BMA | 110/33 | 90 | 0.0039 | 0.2463 | 1.1 | 0.8 | 19
WOO | T4201 | 500 | 400/220 | 0.0002 | 0.0316 | 0.014 | 0.155 | CPS IBTx 1 | 275/110 | 0.002 | 0.064 | 0.002 | 0.224 | 0 | 0.145 | 240 | 240 | 60 | 1.15 | 0.85 | 19 | BMA | 110/33 | 90 | 0.0065 | 0.2893 | 1.1 | 0.8 | 19
WOO | T4202 | 550 | 400/220 | 0.0002 | 0.027 | N/A | N/A | CPS IBTx 2 | 275/110 | 0.001 | 0.064 | 0.001 | 0.224 | 0 | 0.145 | 240 | 240 | 30 | 1.15 | 0.85 | 19 | BMA | 110/33 | 60 | 0.0065 | 0.2867 | 1.1 | 0.8 | 19
WOO | T4204 | 500 | 400/220 | 0.0002 | 0.0316 | 0.014 | 0.155 | HAN IBTx 1 | 275/110 | 0.002 | 0.059 | 0.002 | 0.126 | 0 | 0.056 | 240 | 240 | 45 | 1.15 | 0.85 | 19 | BAN (N) | 110/33 | 30 | 0.0171 | 0.4133 | 1.1 | 0.8 | 15
LOU | AT1 | 300 | 275/220 | 0.0008 | 0.0303 | 0.154 | 0.154 | HAN IBTx 2 | 275/110 | 0.002 | 0.059 | 0.002 | 0.126 | 0 | 0.056 | 240 | 240 | 45 | 1.15 | 0.85 | 19 | BAN (N) | 110/33 | 30 | 0.019 | 0.414 | 1.1 | 0.8 | 15
LOU | AT2 | 600 | 220/275 | 0.0008 | 0.03 | 0.154 | 0.154 | HAN IBTx 3 | 275/110 | 0.001 | 0.064 | 0.001 | 0.224 | 0 | 0.145 | 240 | 240 | 60 | 1.15 | 0.85 | 19 | BAN (N) | 110/33 | 30 | 0.019 | 0.4167 | 1.1 | 0.8 | 15
LOU | AT3 | 300 | 220/275 | 0.0008 | 0.015 | 0.154 | 0.154 | KEL IBTx 1 | 275/110 | 0.002 | 0.061 | 0.002 | 0.127 | 0 | 0.057 | 240 | 240 | 45 | 1.15 | 0.85 | 19 | BAN (N) | 110/33 | 30 | 0.019 | 0.415 | 1.1 | 0.8 | 15
AD | T2101 | 125 | 220/110 | 0.001 | 0.124 | 0.1 | 0.18 | KEL IBTx 2 | 275/110 | 0.002 | 0.061 | 0.002 | 0.132 | 0 | 0.057 | 240 | 240 | 45 | 1.15 | 0.85 | 19 | BNH | 110/33 | 90 | 0.0037 | 0.2419 | 1.1 | 0.8 | 19
ARK | T2101 | 63 | 220/110 | 0.007 | 0.18 | 0.23 | 0.19 | TAN IBTx 1 | 275/110 | 0.002 | 0.064 | 0.002 | 0.209 | 0 | 0.133 | 240 | 240 | 30 | 1.15 | 0.85 | 19 | BNH | 110/33 | 90 | 0.0038 | 0.2413 | 1.1 | 0.8 | 19
ARK | T2102 | 125 | 220/110 | 0.0021 | 0.1237 | 0.097 | 0.182 | TAN IBTx 2 | 275/110 | 0.002 | 0.064 | 0.002 | 0.209 | 0 | 0.133 | 240 | 240 | 30 | 1.15 | 0.85 | 19 | BNM | 110/33 | 90 | 0.0039 | 0.2461 | 1.1 | 0.8 | 19
BVK | T2101 | 250 | 220/110 | 0.001 | 0.064 | 0.097 | 0.178 | TAN IBTx 3 | 275/110 | 0.001 | 0.064 | 0.001 | 0.224 | 0 | 0.145 | 240 | 240 | 60 | 1.15 | 0.85 | 19 | BNM | 110/33 | 90 | 0.0039 | 0.2461 | 1.1 | 0.8 | 19
BVK | T2102 | 250 | 220/110 | 0.001 | 0.064 | 0.097 | 0.178 | TMN IBTx 1 | 275/110 | 0.001 | 0.064 | 0.004 | 0.232 | 0 | 0.151 | 240 | 240 | 60 | 1.15 | 0.85 | 19 | BRO | 110/33 | 100 | 0.0035 | 0.16 | 1.1 | 0.9 | 33
BLC | T2101 | 250 | 220/110 | 0.001 | 0.0646 | 0.097 | 0.179 | TMN IBTx 2 | 275/110 | 0.001 | 0.064 | 0.004 | 0.23 | 0 | 0.15 | 240 | 240 | 60 | 1.15 | 0.85 | 19 | CAR | 110/33 | 90 | 0.0039 | 0.248 | 1.1 | 0.8 | 19
CLA | T2102 | 250 | 220/110 | 0.0013 | 0.0647 | 0.097 | 0.179 | KPS IBTx 1 | 275/11.5 | 0.006 | 0.307 | 0.009 | 0.574 | 0.06 | 0.304 | 110 | 55 | 55 | 1.15 | 0.938 | 33 | CAR | 110/33 | 90 | 0.0039 | 0.248 | 1.1 | 0.8 | 19
CLA | T2101 | 250 | 220/110 | 0.0013 | 0.0647 | 0.1 | 0.1 | [14 empty] | CEN | 110/33 | 90 | 0.0037 | 0.2422 | 1.1 | 0.8 | 19
CSH | T2101 | 238 | 220/110 | 0.0004 | 0.0631 | 0.096 | 0.182 | [14 empty] | CEN | 110/33 | 90 | 0.0038 | 0.2419 | 1.1 | 0.8 | 19
CSH | T2102 | 250 | 220/110 | 0.0004 | 0.0631 | 0.096 | 0.182 | [14 empty] | COL (N) | 110/33 | 60 | 0.0074 | 0.2512 | 1.1 | 0.8 | 19
CSH | T2104 | 175 | 220/110 | 0.0021 | 0.1332 | 0.227 | 0.182 | [14 empty] | COL (N) | 110/33 | 60 | 0.0075 | 0.2508 | 1.1 | 0.8 | 19
CKM | T2101 | 250 | 220/110 | 0.001 | 0.0646 | 0.097 | 0.179 | [14 empty] | CPS | 110/33 | 90 | 0.0087 | 0.2559 | 1.1 | 0.8 | 19
CKM | T2102 | 250 | 220/110 | 0.001 | 0.0646 | 0.097 | 0.179 | [14 empty] | CPS | 110/33 | 90 | 0.0087 | 0.2573 | 1.1 | 0.8 | 19
CKM | T2103 | 250 | 220/110 | 0.001 | 0.0646 | 0.097 | 0.179 | [14 empty] | CRG | 110/33 | 60 | 0.0074 | 0.2515 | 1.1 | 0.8 | 19
CKM | T2104 | 250 | 220/110 | 0.0004 | 0.0631 | 0.096 | 0.182 | [14 empty] | CRG | 110/33 | 60 | 0.0074 | 0.2508 | 1.1 | 0.8 | 19
CUL | T2101 | 250 | 220/110 | 0.0005 | 0.064 | 0.09 | 0.182 | [14 empty] | CRE | 110/33 | 75 | 0.0091 | 0.1953 | 1.1 | 0.8 | 19
CDU | T2101 | 250 | 220/110 | 0.00093 | 0.06152 | 0.097 | 0.178 | [14 empty] | CRE | 110/33 | 75 | 0.0091 | 0.1967 | 1.1 | 0.8 | 19
CDU | T2102 | 250 | 220/110 | 0.00066 | 0.061 | 0.099 | 0.177 | [14 empty] | DON | 110/33 | 60 | 0.0119 | 0.3607 | 1.1 | 0.8 | 19
FLA | T2101 | 125 | 220/110 | 0.0027 | 0.128 | 0.097 | 0.182 | [14 empty] | DON | 110/33 | 60 | 0.0119 | 0.3658 | 1.1 | 0.8 | 19
FLA | T2102 | 125 | 220/110 | 0.0008 | 0.1331 | 0.097 | 0.182 | [14 empty] | DON | 110/33 | 90 | 0.004 | 0.2403 | 1.1 | 0.8 | 19
FIN | T2101 | 250 | 220/110 | 0.0013 | 0.0651 | 0.098 | 0.18 | [14 empty] | DON | 110/33 | 60 | 0.0119 | 0.3658 | 1.1 | 0.8 | 19
FIN | T2102 | 250 | 220/110 | 0.0013 | 0.0648 | 0.099 | 0.18 | [14 empty] | DRU (N) | 110/33 | 90 | 0.0061 | 0.2423 | 1.1 | 0.8 | 19
FIN | T2103 | 250 | 220/110 | 0.001 | 0.064 | 0.099 | 0.177 | [14 empty] | DRU (N) | 110/33 | 90 | 0.0061 | 0.2426 | 1.1 | 0.8 | 19
FIN | T2104 | 250 | 220/110 | 0.001 | 0.0638 | 0.099 | 0.177 | [14 empty] | DRQ | 110/33 | 90 | 0.0039 | 0.2461 | 1.1 | 0.8 | 19
FIN | T2105 | 250 | 220/110 | 0.001 | 0.064 | 0.099 | 0.177 | [14 empty] | DUN | 110/33 | 90 | 0.0087 | 0.2566 | 1.1 | 0.8 | 19
GI | T2101 | 125 | 220/110 | 0.0026 | 0.1331 | 0.097 | 0.182 | [14 empty] | DUN | 110/33 | 90 | 0.0087 | 0.2599 | 1.1 | 0.8 | 19
GI | T2102 | 125 | 220/110 | 0.0023 | 0.1237 | 0.229 | 0.182 | [14 empty] | EDE | 110/33 | 45 | 0.0125 | 0.2733 | 1.1 | 0.8 | 19
GOR | T2101 | 250 | 220/110 | 0.001 | 0.064 | 0.097 | 0.182 | [14 empty] | EDE | 110/33 | 45 | 0.0123 | 0.2738 | 1.1 | 0.8 | 19
INC | T2101 | 250 | 220/110 | 0.001 | 0.0564 | 0.095 | 0.178 | [14 empty] | ENN (N) | 110/33 | 45 | 0.0126 | 0.272 | 1.1 | 0.8 | 19
INC | T2102 | 250 | 220/110 | 0.001 | 0.0564 | 0.095 | 0.178 | [14 empty] | ENN (N) | 110/33 | 45 | 0.0126 | 0.2733 | 1.1 | 0.8 | 19
INC | T2103 | 250 | 220/110 | 0.0001 | 0.06 | 0.09 | 0.182 | [14 empty] | ENN (N) | 110/33 | 60 | 0.0078 | 0.2512 | 1.1 | 0.8 | 19
INC | T2104 | 250 | 220/110 | 0.0001 | 0.06 | 0.09 | 0.182 | [14 empty] | FIN (N) | 110/33 | 45 | 0.0076 | 0.2533 | 1.1 | 0.8 | 19
KNR | T2101 | 250 | 220/110 | 0.001 | 0.064 | 0.097 | 0.178 | [14 empty] | FIN (N) | 110/33 | 45 | 0.0076 | 0.2549 | 1.1 | 0.8 | 19
KNR | T2102 | 250 | 220/110 | 0.001 | 0.064 | 0.097 | 0.178 | [14 empty] | GLE (N) | 110/33 | 60 | 0.0119 | 0.2692 | 1.1 | 0.8 | 19
KRA | T2101 | 250 | 220/110 | 0.0013 | 0.0647 | 0.097 | 0.179 | [14 empty] | GOR (N) | 110/33 | 90 | 0.0039 | 0.2461 | 1.1 | 0.8 | 19
KRA | T2102 | 250 | 220/110 | 0.0013 | 0.0652 | 0.097 | 0.179 | [14 empty] | KMT | 110/33 | 90 | 0.0039 | 0.2461 | 1.1 | 0.8 | 19
KRA | T2103 | 250 | 220/110 | 0.0013 | 0.0652 | 0.097 | 0.179 | [14 empty] | KNO | 110/33 | 90 | 0.0039 | 0.2461 | 1.1 | 0.8 | 19
KLN | T2101 | 63 | 220/110 | 0.0065 | 0.2453 | 0.229 | 0.182 | [14 empty] | KNO | 110/33 | 90 | 0.0039 | 0.2461 | 1.1 | 0.8 | 19
KLN | T2102 | 63 | 220/110 | 0.0095 | 0.2473 | 0.229 | 0.182 | [14 empty] | LAR | 110/33 | 45 | 0.0116 | 0.2778 | 1.1 | 0.8 | 15
KLN | T2103 | 250 | 220/110 | 0.0004 | 0.0631 | 0.096 | 0.182 | [14 empty] | LAR | 110/33 | 45 | 0.0116 | 0.2771 | 1.1 | 0.8 | 15
KLN | T2104 | 120 | 220/110 | 0.001 | 0.123 | 0.097 | 0.182 | [14 empty] | LIM (N) | 110/33 | 45 | 0.0125 | 0.2809 | 1.1 | 0.8 | 15
BYH | T2101 | 250 | 220/110 | 0.001 | 0.064 | 0.097 | 0.178 | [14 empty] | LIM (N) | 110/33 | 45 | 0.0122 | 0.2764 | 1.1 | 0.8 | 15
BYH | T2102 | 250 | 220/110 | 0.001 | 0.064 | 0.097 | 0.178 | [14 empty] | LIS (N) | 110/33 | 90 | 0.0087 | 0.254 | 1.1 | 0.8 | 19
KLS | T2101 | 125 | 220/110 | 0.00132 | 0.1237 | 0.097 | 0.182 | [14 empty] | LIS (N) | 110/33 | 90 | 0.0086 | 0.2569 | 1.1 | 0.8 | 19
KLS | T2102 | 125 | 220/110 | 0.0008 | 0.1237 | 0.097 | 0.182 | [14 empty] | LMR | 110/33 | 45 | 0.0076 | 0.254 | 1.1 | 0.8 | 19
KPG | T2101 | 250 | 220/110 | 0.0004 | 0.0631 | 0.096 | 0.182 | [14 empty] | LMR | 110/33 | 45 | 0.0076 | 0.2533 | 1.1 | 0.8 | 19
KPG | T2102 | 250 | 220/110 | 0.0004 | 0.0631 | 0.096 | 0.182 | [14 empty] | LOG | 110/33 | 45 | 0.0126 | 0.2738 | 1.1 | 0.8 | 19
CBT | T2101 | 250 | 220/110 | 0.001 | 0.0646 | 0.097 | 0.179 | [14 empty] | LOG | 110/33 | 45 | 0.0128 | 0.28 | 1.1 | 0.8 | 19
CBT | T2102 | 250 | 220/110 | 0.001 | 0.0646 | 0.097 | 0.179 | [14 empty] | MKL | 110/33 | 90 | 0.0039 | 0.2502 | 1.1 | 0.8 | 19
CBT | T2103 | 250 | 220/110 | 0.001 | 0.0646 | 0.097 | 0.179 | [14 empty] | MKL | 110/33 | 90 | 0.0039 | 0.2502 | 1.1 | 0.8 | 19
CBT | T2104 | 250 | 220/110 | 0.001 | 0.0646 | 0.097 | 0.179 | [14 empty] | NAR | 110/33 | 60 | 0.0075 | 0.2505 | 1.1 | 0.8 | 19
LOU | T2101 | 125 | 220/110 | 0.0022 | 0.1331 | 0.229 | 0.182 | [14 empty] | NAR | 110/33 | 60 | 0.0073 | 0.25 | 1.1 | 0.8 | 19
LOU | T2103 | 125 | 220/110 | 0.0023 | 0.1324 | 0.229 | 0.182 | [14 empty] | NEW (N) | 110/33 | 90 | 0.0038 | 0.2427 | 1.1 | 0.8 | 19
LOU | T2102 | 125 | 220/110 | 0.0022 | 0.1324 | 0.23 | 0.182 | [14 empty] | NEW (N) | 110/33 | 90 | 0.0038 | 0.2419 | 1.1 | 0.8 | 19
LOU | T2104 | 250 | 220/110 | 0.001 | 0.064 | 0.097 | 0.178 | [14 empty] | OMA | 110/33 | 90 | 0.0039 | 0.2481 | 1.1 | 0.8 | 19
LWD | T2101 | 250 | 220/110 | 0.001 | 0.064 | 0.099 | 0.18 | [14 empty] | OMA | 110/33 | 90 | 0.0039 | 0.249 | 1.1 | 0.8 | 19
MAY | T2101 | 125 | 220/110 | 0.0021 | 0.1339 | 0.227 | 0.182 | [14 empty] | RSK | 110/33 | 90 | 0.0039 | 0.2461 | 1.1 | 0.8 | 19
MAY | T2102 | 238 | 220/110 | 0.001 | 0.064 | 0.097 | 0.178 | [14 empty] | RAT (N) | 110/33 | 90 | 0.0087 | 0.2549 | 1.1 | 0.8 | 19
MAY | T2103 | 125 | 220/110 | 0.0021 | 0.1324 | 0.227 | 0.182 | [14 empty] | RAT (N) | 110/33 | 90 | 0.0046 | 0.2402 | 1.1 | 0.8 | 19
MAY | T2104 | 250 | 220/110 | 0.001 | 0.064 | 0.099 | 0.177 | [14 empty] | ROS | 110/33 | 90 | 0.0087 | 0.2576 | 1.1 | 0.8 | 19
MP | T2101 | 250 | 220/110 | 0.001 | 0.064 | 0.097 | 0.178 | [14 empty] | ROS | 110/33 | 90 | 0.0087 | 0.2533 | 1.1 | 0.8 | 19
PB | T2103 | 250 | 220/110 | 0.0013 | 0.059 | 0.089 | 0.173 | [14 empty] | SPR | 110/33 | 90 | 0.0039 | 0.247 | 1.1 | 0.8 | 19
PB | T2104 | 250 | 220/110 | 0.0013 | 0.0609 | 0.089 | 0.173 | [14 empty] | SPR | 110/33 | 90 | 0.0039 | 0.2471 | 1.1 | 0.8 | 19
RAF | T2101 | 238 | 220/110 | 0.001 | 0.064 | 0.097 | 0.178 | [14 empty] | STR (N) | 110/33 | 45 | 0.0076 | 0.2522 | 1.1 | 0.8 | 19
RAF | T2102 | 250 | 220/110 | 0.000446 | 0.0558 | 0.097 | 0.178 | [14 empty] | STR (N) | 110/33 | 45 | 0.0076 | 0.2516 | 1.1 | 0.8 | 19
SH | T2101 | 125 | 220/110 | 0.00574 | 0.1237 | 0.097 | 0.182 | [14 empty] | TRE | 110/33 | 90 | 0.0039 | 0.2461 | 1.1 | 0.8 | 19
SH | T2102 | 125 | 220/110 | 0.00131 | 0.1237 | 0.097 | 0.182 | [14 empty] | WAR | 110/33 | 90 | 0.0039 | 0.2481 | 1.1 | 0.8 | 19
SRA | T2101 | 250 | 220/110 | 0.001 | 0.064 | 0.097 | 0.182 | [14 empty] | WAR | 110/33 | 90 | 0.0039 | 0.2488 | 1.1 | 0.8 | 19
TB | T2101 | 238 | 220/110 | 0.00099 | 0.0554 | 0.097 | 0.179
TB | T2102 | 238 | 220/110 | 0.00099 | 0.0554 | 0.097 | 0.179

## power flow controllers
Table B-6 Characteristics of Existing Power Flow Controllers
| Voltage (kV) |  | Rating (MVA) | Impedance on |  | Phase Angle Range
Station |  | Circuit |  | 100 MVA Base (pu) |  | (electrical degrees)
|  |  |  | R | X | + | -
CKM | 220 | CKM – PB | 350 | 0 | 0.029 | 15.3 | 15.3
ENN (N) | 110 | ENN (N) – | 125 | 0 | 0.0213 | 45 | 45
COR
STR (N) | 110 | STR (N) – | 125 | 0 | 0.0213 | 45 | 45
LET

## reactive compensation
Table B-7 Characteristics of Existing Reactive Compensation
Capability (Mvar)
Station | Voltage (kV) | Plant | Generate | Absorb
AA | 110 | 1 Capacitor | 30
ATH | 110 | 3 Capacitors (1 Mobile) | 90
BAN (I) | 110 | 1 Capacitor | 15
BYC | 275 | 4 Capacitors (4 x 59) | 236
CAH | 110 | 4 Capacitors (4 x 15) | 60
CAS | 22 | 1 Shunt Reactor (30) |  | 30
CAS | 22 | 3 Capacitors (3 x 25) | 75
CBR | 110 | 1 Capacitor | 30
CBR | 110 | 1 Static Var Compensator | 10 | 60
CF | 110 | 1 Capacitor | 15
CGL | 20 | 3 Capacitors (3 x 1) | 3
CKM | 220 | 1 Shunt Reactor |  | 100
CKM | 38 | 1 Shunt Reactor |  | 20
COL (N) | 110 | 1 Capacitor | 36
CPS | 110 | 1 Capacitor | 40
CSH | 110 | 2 Capacitors (2 x 40) | 80
CUN | 20 | 2 Capacitors (2 x 4) | 8
DLN | 33 | 1 Capacitor | 5
DLT | 110 | 1 Capacitor | 15
DMY | 110 | 1 Capacitor | 15
DOO | 110 | 1 Capacitor | 15
DRU (I) | 110 | 1 Capacitor | 15
DYN | 20 | 2 Capacitors (2 x 6.5) | 13
ENN (N) | 33 | 4 Capacitors (4 x 6) | 24
FIN (I) | 38 | 1 Shunt Reactor |  | 20
GRV | 20 | 1 Static Var Compensator | 7.5 | 7.5
GRV | 20 | 2 Capacitors (1 x 12.38, 1 x 1.5) | 13.9
GRV | 20 | 1 Shunt Reactor |  | 9
GIL | 20 | 1 Capacitor | 12
GWE | 110 | 1 Capacitor | 15
HAN | 22 | 2 Shunt Reactors (2 x 30) |  | 60
INC | 38 | 2 Shunt Reactors (2 x 20) |  | 40
KEL | 22 | 2 Shunt Reactors (2 x 30) |  | 60
KKY | 110 | 2 Capacitor (2 x 15) | 30
KNR | 220 | 1 Shunt Reactor |  | 50
KNY | 110 | 1 Capacitor | 30
KTL | 110 | 1 Capacitor | 30
LET | 110 | 2 Capacitor (1 Mobile) | 45
LET | 110 | 1 Static Var Compensator | 30
LIS (I) | 110 | 2 Capacitors (2 x 15) | 30
LOU | 110 | 1 Capacitor | 30
LSN | 20 | 1 Capacitor | 4
MOY | 110 | 2 Capacitors (2 x 15) | 30
MP | 6.6 | 1 Capacitor | 1
MRY | 20 | 1 Capacitor | 4
MUL | 110 | 2 Capacitors (2 x 15) | 30
NAV | 110 | 1 Capacitor (1 Mobile) | 30
PB | 220 | 2 Shunt Reactors (2 x 50) |  | 100
POR | 400 | EWIC HVDC | 175 | 175
RAF | 110 | 1 Capacitor | 60
RE | 38 | 1 Shunt Reactor |  | 20
SKL | 110 | 1 Capacitor (1 Mobile) | 30
SLB | 20 | 1 Capacitor | 15
SLI | 110 | 1 Capacitor | 15
SLK | 20 | 1 Capacitor | 13
TAN | 22 | 2 Capacitors (2 x 25) | 50
TAN | 22 | 2 Shunt Reactors (2 x 30) |  | 60
THU | 110 | 1 Capacitor | 15
THU | 110 | 1 Static Var Compensator | 30 | 30
TRI | 110 | 1 Capacitor | 30
TRL | 110 | 1 Capacitor | 30
WEX | 110 | 2 Capacitors (2 x 15) | 30

## demand
Table C-1 Demand Forecasts at Time of Winter Peak | [12 empty] | Table C-2 Demand Forecasts at Time of Summer Peak | [12 empty] | Table C-3 Demand Forecasts at Time of Summer Valley | [12 empty] | Table C-4 Demand Forecasts at Time of Autumn Peak – Northern Ireland only
Bus Code | Bus Name | Power Factor | Demand Forecast (MW) | [9 empty] | Bus Code | Bus Name | Power Factor | Demand Forecast (MW) | [9 empty] | Bus Code | Bus Name | Power Factor | Demand Forecast (MW) | [9 empty] | Bus Code | Bus Name | Power Factor | Demand Forecast (MW)
|  |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  |  |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  |  |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  |  |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
AA | Ardnacrusha | 0.992 | 63.2 | 64.6 | 64.2 | 64.4 | 64.5 | 64.7 | 65.1 | 65.6 | 66.4 | 66.8 | AA | Ardnacrusha | 0.993 | 48.8 | 49.7 | 49.3 | 48.6 | 48.5 | 48.4 | 48.6 | 48.9 | 49.3 | 49.5 | AA | Ardnacrusha | 1 | 28.7 | 28.7 | 28.6 | 28.5 | 28.5 | 28.5 | 28.4 | 28.4 | 28.4 | 28.4 | AGH | Aghyoule | 0.99 | 14.9 | 15.2 | 15.1 | 15.5 | 15.7 | 15.9 | 16 | 16.1 | 16.2 | 16.3
AGH | Aghyoule | 0.99 | 17.1 | 17.5 | 17.4 | 17.9 | 18.1 | 18.3 | 18.4 | 18.5 | 18.6 | 18.7 | AGH | Aghyoule | 0.99 | 5 | 5.1 | 5.1 | 5.2 | 5.3 | 5.4 | 5.4 | 5.4 | 5.5 | 5.5 | AGH (N) | Aghyoule | 0.99 | 5 | 5.1 | 5.1 | 5.2 | 5.3 | 5.4 | 5.4 | 5.4 | 5.5 | 5.5 | AIR | Airport Road | 0.99 | - | - | 24.5 | 26.5 | 27.7 | 29.1 | 32.5 | 32.7 | 32.9 | 33
AGN | Aungierstown | 0.95 | - | 7.6 | 15.2 | 22.8 | 25.2 | 27.6 | 29.9 | 32.3 | 34.7 | 37.1 | AGN | Aungierstown | 0.95 | 0 | 7.6 | 15.2 | 22.8 | 25.2 | 27.6 | 29.9 | 32.3 | 34.7 | 37.1 | AGN | Aungierstown | 0.95 | 0 | 7.6 | 15.2 | 22.8 | 25.2 | 27.6 | 29.9 | 32.3 | 34.7 | 37.1 | ANT | Antrim | 0.98 | 36.4 | 37 | 36.7 | 37.5 | 37.7 | 37.9 | 38.1 | 38.3 | 38.5 | 38.8
AGY | Ardnagappary | 1 | 16.1 | 16.41 | 16.31 | 16.36 | 16.38 | 16.44 | 16.54 | 16.67 | 16.86 | 16.97 | AGY | Ardnagappary | 0.989 | 11 | 11.2 | 11.1 | 10.9 | 10.9 | 10.9 | 10.9 | 11 | 11.1 | 11.1 | AGY | Ardnagappary | 0.98 | 4.8 | 4.8 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | BAN (N) | Banbridge | 0.99 | 34.1 | 34.7 | 34.4 | 35.1 | 35.3 | 35.6 | 35.7 | 35.9 | 36.1 | 36.3
AHA | Ahane | 0.999 | 5 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.2 | 5.2 | 5.3 | 5.3 | AHA | Ahane | 0.998 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.8 | 3.9 | 3.9 | 3.9 | 3.9 | AHA | Ahane | 0.965 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | BMA | Ballymena | 0.96 | 72.7 | 74 | 73.3 | 74.9 | 75.4 | 75.8 | 76.1 | 76.6 | 77 | 77.4
AIR | Airport Road | 0.99 | - | - | 28.2 | 30.5 | 31.9 | 33.5 | 37.4 | 37.6 | 37.8 | 38 | AIR | Airport Road | 0.99 |  |  | 8.3 | 8.9 | 9.4 | 9.8 | 11 | 11 | 11.1 | 11.1 | AIR | Airport Road | 0.99 | - | - | 8.3 | 8.9 | 9.4 | 9.8 | 11 | 11 | 11.1 | 11.1 | BNH | Ballynahinch | 0.99 | 49.5 | 50.4 | 49.9 | 51 | 51.3 | 51.6 | 51.8 | 52.1 | 52.4 | 52.7
ANR | Anner | 0.95 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | ANR | Anner | 0.95 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | ANR | Anner | 0.95 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | BNM | Belfast North | 0.99 | 43.5 | 44.4 | 43.9 | 44.9 | 45.2 | 45.4 | 45.6 | 45.9 | 46.1 | 46.4
ANT | Antrim | 0.98 | 41.8 | 42.6 | 42.2 | 43.1 | 43.4 | 43.7 | 43.9 | 44.1 | 44.4 | 44.6 | ANT | Antrim | 0.98 | 12.3 | 12.5 | 12.4 | 12.6 | 12.7 | 12.8 | 12.9 | 12.9 | 13 | 13.1 | ANT | Antrim | 0.98 | 12.3 | 12.5 | 12.4 | 12.6 | 12.7 | 12.8 | 12.9 | 12.9 | 13 | 13.1 | BVG | Ballyvallagh | 0.99 | 13.2 | 13.4 | 13.3 | 13.6 | 13.6 | 13.7 | 13.8 | 13.8 | 13.9 | 14
ARI | Arigna | 1 | 5.5 | 5.6 | 5.6 | 5.6 | 5.6 | 5.7 | 5.7 | 5.7 | 5.8 | 5.8 | ARI | Arigna | 0.998 | 4.3 | 4.3 | 4.3 | 4.3 | 4.2 | 4.2 | 4.3 | 4.3 | 4.3 | 4.3 | ARI | Arigna | 0.911 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | CAR | Carnmoney | 0.99 | 21.8 | 21.9 | 21.4 | 21.5 | 21.3 | 21.1 | 20.9 | 21 | 21.1 | 21.2
ARK | Arklow | 1 | 41.7 | 42.6 | 42.3 | 42.4 | 42.5 | 42.6 | 42.9 | 43.2 | 43.7 | 44 | ARK | Arklow | 0.997 | 32.2 | 32.7 | 32.5 | 32.1 | 31.9 | 31.9 | 32 | 32.2 | 32.5 | 32.6 | ARK | Arklow | 0.967 | 15.4 | 15.4 | 15.4 | 15.4 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | CEN | Belfast Central | 0.99 | 46.2 | 47.1 | 46.8 | 47.9 | 48.2 | 48.6 | 48.9 | 49.2 | 49.4 | 49.7
ATH | Athlone | 0.997 | 82.1 | 83.9 | 83.3 | 83.6 | 83.7 | 84 | 84.5 | 85.2 | 86.2 | 86.7 | ATH | Athlone | 0.998 | 63.4 | 64.5 | 64 | 63.2 | 62.9 | 62.9 | 63.1 | 63.5 | 64 | 64.2 | ATH | Athlone | 0.995 | 26.8 | 26.7 | 26.7 | 26.6 | 26.6 | 26.6 | 26.5 | 26.5 | 26.5 | 26.5 | COL (N) | Coleraine | 0.99 | 37.1 | 37.8 | 37.5 | 38.3 | 38.5 | 38.7 | 38.8 | 39.1 | 39.3 | 39.5
ATY | Athy | 0.966 | 19.4 | 19.8 | 19.7 | 19.7 | 19.8 | 19.8 | 19.9 | 20.1 | 20.3 | 20.5 | ATY | Athy | 0.968 | 15 | 15.2 | 15.1 | 14.9 | 14.9 | 14.8 | 14.9 | 15 | 15.1 | 15.2 | ATY | Athy | 0.971 | 6.1 | 6.1 | 6.1 | 6.1 | 6 | 6 | 6 | 6 | 6 | 6 | CPS | Coolkeeragh | 0.99 | 22 | 22.4 | 22.2 | 22.7 | 22.9 | 23 | 23.1 | 23.2 | 23.3 | 23.5
BAG | Barnageeragh | 0.95 | - | - | 2.4 | 4.8 | 7.1 | 9.5 | 11.9 | 14.3 | 16.6 | 19 | BAG | Barnageeragh | 0.95 | 0 | 0 | 2.4 | 4.8 | 7.1 | 9.5 | 11.9 | 14.3 | 16.6 | 19 | BAG | Barnageeragh | 0.95 | 0 | 0 | 2.4 | 4.8 | 7.1 | 9.5 | 11.9 | 14.3 | 16.6 | 19 | CRE | Cregagh | 0.99 | 74.9 | 63 | 62.5 | 64 | 64.5 | 64.9 | 65.3 | 65.7 | 66.1 | 66.5
BAL | Baltrasna | 0.999 | 16.5 | 16.8 | 16.7 | 16.8 | 16.8 | 16.9 | 17 | 17.1 | 17.3 | 17.4 | BAL | Baltrasna | 1 | 12.7 | 12.9 | 12.8 | 12.7 | 12.6 | 12.6 | 12.7 | 12.7 | 12.8 | 12.9 | BAL | Baltrasna | 0.998 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | CRG | Creagh | 0.99 | 21.6 | 22 | 21.8 | 22.3 | 22.4 | 22.5 | 22.6 | 22.8 | 22.9 | 23
BAN | Bandon | 0.989 | 48.8 | 49.9 | 49.6 | 49.7 | 49.8 | 50 | 50.3 | 50.7 | 51.3 | 51.6 | BAN | Bandon | 0.987 | 37.7 | 38.4 | 38.1 | 37.6 | 37.4 | 37.4 | 37.5 | 37.7 | 38 | 38.2 | BAN | Bandon | 0.993 | 16.6 | 16.6 | 16.6 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.4 | DON | Donegall | 0.99 | 79.4 | 79.5 | 77.4 | 77.8 | 77 | 76.2 | 75.3 | 75.7 | 76.2 | 76.6
BAN (N) | Banbridge | 0.99 | 39.2 | 40 | 39.6 | 40.4 | 40.7 | 40.9 | 41.1 | 41.3 | 41.6 | 41.8 | BAN (N) | Banbridge | 0.99 | 11.5 | 11.7 | 11.6 | 11.8 | 11.9 | 12 | 12 | 12.1 | 12.2 | 12.2 | BAN (N) | Banbridge | 0.99 | 11.5 | 11.7 | 11.6 | 11.8 | 11.9 | 12 | 12 | 12.1 | 12.2 | 12.2 | DRU (N) | Drumnakelly | 0.98 | 79.6 | 81.2 | 80.4 | 82.2 | 82.7 | 83.3 | 83.8 | 84.3 | 84.8 | 85.2
BAR | Barrymore | 0.998 | 31.6 | 32.3 | 32.1 | 32.2 | 32.2 | 32.3 | 32.5 | 32.8 | 33.2 | 33.4 | BAR | Barrymore | 1 | 24.4 | 24.8 | 24.6 | 24.3 | 24.2 | 24.2 | 24.3 | 24.4 | 24.6 | 24.7 | BAR | Barrymore | 0.958 | 11.5 | 11.5 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.3 | DUN | Dungannon | 0.99 | 84.3 | 85.9 | 85.1 | 86.9 | 87.4 | 88 | 88.3 | 88.8 | 89.3 | 89.8
BDA | Baroda | 0.95 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | BDA | Baroda | 0.95 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | BDA | Baroda | 0.95 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | EDE | Eden | 0.98 | 30.1 | 30.6 | 30.3 | 31 | 31.2 | 31.4 | 31.5 | 31.7 | 31.8 | 32
BDN | Ballydine | 0.95 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | BDN | Ballydine | 0.95 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | BDN | Ballydine | 0.982 | 3.8 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | ENN (N) | Enniskillen | 0.99 | 49.3 | 50.3 | 49.8 | 50.9 | 51.2 | 51.5 | 51.7 | 52 | 52.3 | 52.6
BDN | Ballydine | 0.984 | 15.2 | 15.5 | 15.4 | 15.5 | 15.5 | 15.5 | 15.6 | 15.8 | 16 | 16 | BDN | Ballydine | 0.96 | 11.7 | 11.9 | 11.8 | 11.7 | 11.6 | 11.6 | 11.7 | 11.7 | 11.8 | 11.9 | BDN | Ballydine | 0.95 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | FIN (N) | Finaghy | 0.99 | 26.9 | 27.4 | 27.2 | 27.7 | 27.9 | 28.1 | 28.2 | 28.3 | 28.5 | 28.7
BEG | Ballybeg | 1 | 15.5 | 15.9 | 15.8 | 15.8 | 15.8 | 15.9 | 16 | 16.1 | 16.3 | 16.4 | BEG | Ballybeg | 1 | 12 | 12.2 | 12.1 | 11.9 | 11.9 | 11.9 | 11.9 | 12 | 12.1 | 12.2 | BEG | Ballybeg | 0.992 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | GLE (N) | Glengormley | 0.97 | 27.3 | 27.7 | 27.3 | 27.8 | 27.9 | 27.9 | 27.9 | 28.1 | 28.3 | 28.4
BIN | Binbane | 1 | 4.67 | 4.77 | 4.74 | 4.76 | 4.76 | 4.78 | 4.81 | 4.85 | 4.9 | 4.93 | BIN | Binbane | 0.969 | 3.7 | 3.8 | 3.7 | 3.67 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | BIN | Binbane | 0.982 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.1 | 6.1 | 6.1 | 6.1 | KNO | Knock | 0.99 | 44.5 | 39.7 | 39.3 | 40.2 | 40.5 | 40.7 | 40.9 | 41.2 | 41.4 | 41.6
BK | Bellacorick | 0.999 | 6 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.2 | 6.2 | 6.3 | 6.3 | BK | Bellacorick | 0.996 | 4.6 | 4.7 | 4.7 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.7 | 4.7 | BK | Bellacorick | 0.998 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | LAR | Larne | 0.99 | 24.9 | 25.4 | 25.1 | 25.6 | 25.8 | 25.9 | 26 | 26.2 | 26.3 | 26.5
BLC | Belcamp | 0.951 | 58.9 | 68.4 | 77.9 | 87.4 | 96.9 | 106.4 | 108.3 | 108.3 | 108.3 | 108.3 | BLC | Belcamp | 0.95 | 58.9 | 68.4 | 77.9 | 87.4 | 96.9 | 106.4 | 108.3 | 108.3 | 108.3 | 108.3 | BLI | Ballylickey | 0.925 | 6 | 6 | 6 | 6 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | LIM (N) | Limavady | 0.99 | 21.5 | 21.9 | 21.7 | 22.2 | 22.3 | 22.4 | 22.5 | 22.6 | 22.7 | 22.9
BLI | Ballylickey | 0.999 | 14.1 | 14.4 | 14.3 | 14.4 | 14.4 | 14.5 | 14.5 | 14.7 | 14.8 | 14.9 | BLI | Ballylickey | 0.991 | 10.9 | 11.1 | 11 | 10.9 | 10.8 | 10.8 | 10.9 | 10.9 | 11 | 11.1 | BLC | Belcamp | 0.95 | 58.9 | 68.4 | 77.9 | 87.4 | 96.9 | 106.4 | 108.3 | 108.3 | 108.3 | 108.3 | LIS (N) | Lisburn | 0.99 | 64.3 | 65.5 | 64.9 | 66.3 | 66.7 | 67.1 | 67.4 | 67.8 | 68.2 | 68.6
BLK | Blake | 0.994 | 28 | 28.6 | 28.4 | 28.5 | 28.5 | 28.6 | 28.8 | 29 | 29.4 | 29.5 | BLK | Blake | 0.99 | 21.6 | 22 | 21.8 | 21.5 | 21.4 | 21.4 | 21.5 | 21.6 | 21.8 | 21.9 | BLK | Blake | 0.999 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.2 | 8.2 | 8.2 | LMR | Lisaghmore | 0.98 | 28.6 | 29.1 | 28.8 | 29.4 | 29.6 | 29.8 | 29.9 | 30.1 | 30.3 | 30.4
BMA | Ballymena | 0.984 | 83.6 | 85.2 | 84.4 | 86.2 | 86.8 | 87.3 | 87.6 | 88.1 | 88.6 | 89.1 | BMA | Ballymena | 0.96 | 24.5 | 25 | 24.7 | 25.3 | 25.4 | 25.6 | 25.7 | 25.8 | 26 | 26.1 | BMA | Ballymena | 0.96 | 24.5 | 25 | 24.7 | 25.3 | 25.4 | 25.6 | 25.7 | 25.8 | 26 | 26.1 | LOG | Loguestown | 0.98 | 33.9 | 34.5 | 34.2 | 34.9 | 35.1 | 35.3 | 35.5 | 35.7 | 35.9 | 36.1
BNH | Ballynahinch | 0.99 | 57 | 58 | 57.4 | 58.7 | 59 | 59.3 | 59.6 | 59.9 | 60.3 | 60.6 | BNH | Ballynahinch | 0.99 | 16.7 | 17 | 16.8 | 17.2 | 17.3 | 17.4 | 17.5 | 17.6 | 17.7 | 17.8 | BNH | Ballynahinch | 0.99 | 16.7 | 17 | 16.8 | 17.2 | 17.3 | 17.4 | 17.5 | 17.6 | 17.7 | 17.8 | NAR | Newtownards | 0.99 | 39.4 | 40.2 | 39.8 | 40.6 | 40.9 | 41.1 | 41.2 | 41.5 | 41.7 | 41.9
BNM | Belfast North | 0.99 | 50.1 | 51 | 50.6 | 51.7 | 52 | 52.3 | 52.5 | 52.8 | 53.1 | 53.4 | BNM | Belfast North | 0.99 | 14.7 | 15 | 14.8 | 15.1 | 15.2 | 15.3 | 15.4 | 15.5 | 15.6 | 15.6 | BNM | Belfast North | 0.99 | 14.7 | 15 | 14.8 | 15.1 | 15.2 | 15.3 | 15.4 | 15.5 | 15.6 | 15.6 | NEW (N) | Newry | 0.99 | 69.5 | 70.8 | 70.2 | 71.7 | 72.1 | 72.6 | 72.9 | 73.3 | 73.7 | 74.1
BOG | Banoge | 0.997 | 8.6 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.9 | 9 | 9.1 | 9.1 | BOG | Banoge | 0.97 | 6.7 | 6.8 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.7 | 6.8 | BOG | Banoge | 0.989 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | OMA | Omagh | 0.99 | 52.7 | 53.7 | 53.2 | 54.3 | 54.6 | 54.9 | 55.1 | 55.5 | 55.8 | 56.1
BR | Ringsend/Francis St | 0.999 | 49.5 | 50.6 | 50.3 | 50.5 | 50.5 | 50.7 | 51 | 51.4 | 52 | 52.3 | BRI | Brinny | 0.95 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | BRI | Brinny | 0.95 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | RAT (N) | Rathgael | 0.99 | 50.3 | 51.2 | 50.7 | 51.8 | 52.1 | 52.4 | 52.6 | 52.9 | 53.2 | 53.5
BRI | Brinny | 0.95 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | BRY | Barnahely | 0.976 | 27.3 | 27.8 | 27.5 | 27.2 | 27.1 | 27.1 | 27.2 | 27.3 | 27.5 | 27.6 | BRY | Barnahely | 0.982 | 26.6 | 26.6 | 26.5 | 26.5 | 26.4 | 26.4 | 26.4 | 26.3 | 26.3 | 26.3 | ROS | Rosebank | 0.99 | 26.4 | 24.2 | 24 | 24.5 | 24.6 | 24.8 | 24.9 | 25 | 25.2 | 25.3
BRY | Barnahely | 0.977 | 35.3 | 36.1 | 35.9 | 36 | 36 | 36.1 | 36.4 | 36.7 | 37.1 | 37.3 | BUT | Butlerstown | 0.989 | 32.2 | 32.8 | 32.5 | 32.1 | 32 | 31.9 | 32 | 32.2 | 32.5 | 32.6 | BUT | Butlerstown | 0.999 | 12.9 | 12.9 | 12.9 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.7 | SPR | Springtown | 0.98 | 41.3 | 42.1 | 41.7 | 42.6 | 42.8 | 43 | 43.2 | 43.5 | 43.7 | 43.9
BUT | Butlerstown | 0.989 | 41.7 | 42.6 | 42.3 | 42.5 | 42.5 | 42.7 | 42.9 | 43.3 | 43.8 | 44 | BVG | Larne | 0.99 | 4.4 | 4.5 | 4.5 | 4.6 | 4.6 | 4.6 | 4.6 | 4.7 | 4.7 | 4.7 | BVG | Ballyvallagh | 0.99 | 4.4 | 4.5 | 4.5 | 4.6 | 4.6 | 4.6 | 4.6 | 4.7 | 4.7 | 4.7 | STR (N) | Strabane | 0.99 | 36.8 | 37.5 | 37.1 | 37.9 | 38.1 | 38.3 | 38.5 | 38.7 | 38.9 | 39.1
BVG | Ballyvallagh | 0.99 | 15.1 | 15.4 | 15.3 | 15.6 | 15.7 | 15.8 | 15.8 | 15.9 | 16 | 16.1 | CAH | Cahir | 0.981 | 21 | 21.4 | 21.2 | 21 | 20.9 | 20.9 | 21 | 21.1 | 21.2 | 21.3 | CAH | Cahir | 1 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.2 | WAR | Waringstown | 0.99 | 57.5 | 58.6 | 58 | 59.3 | 59.6 | 59.9 | 60.1 | 60.5 | 60.9 | 61.2
CAH | Cahir | 0.989 | 27.3 | 27.8 | 27.7 | 27.8 | 27.8 | 27.9 | 28.1 | 28.3 | 28.6 | 28.8 | CAR | Carnmoney | 0.99 | 7.4 | 7.4 | 7.2 | 7.3 | 7.2 | 7.1 | 7 | 7.1 | 7.1 | 7.2 | CAR | Carnmoney | 0.99 | 7.4 | 7.4 | 7.2 | 7.3 | 7.2 | 7.1 | 7 | 7.1 | 7.1 | 7.2
CAR | Carnmoney | 0.99 | 25.1 | 25.2 | 24.6 | 24.7 | 24.5 | 24.3 | 24 | 24.2 | 24.3 | 24.4 | CBG | Carrowbeg | 0.984 | 14.4 | 14.6 | 14.5 | 14.3 | 14.3 | 14.2 | 14.3 | 14.4 | 14.5 | 14.5 | CBG | Carrowbeg | 0.996 | 8.4 | 8.4 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3
CBG | Carrowbeg | 0.991 | 18.6 | 19 | 18.9 | 18.9 | 19 | 19 | 19.1 | 19.3 | 19.5 | 19.6 | CBR | Castlebar | 0.988 | 26.5 | 27 | 26.7 | 26.4 | 26.3 | 26.3 | 26.4 | 26.5 | 26.7 | 26.8 | CBR | Castlebar | 0.984 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.6 | 10.6 | 10.6 | 10.6
CBR | Castlebar | 0.993 | 34.3 | 35 | 34.8 | 35 | 35 | 35.1 | 35.3 | 35.6 | 36 | 36.2 | CEN | Belfast Central | 0.99 | 15.6 | 15.9 | 15.8 | 16.1 | 16.3 | 16.4 | 16.5 | 16.6 | 16.7 | 16.8 | CEN | Belfast Central | 0.99 | 15.6 | 15.9 | 15.8 | 16.1 | 16.3 | 16.4 | 16.5 | 16.6 | 16.7 | 16.8
CEN | Belfast Central | 0.99 | 53.2 | 54.2 | 53.8 | 55.1 | 55.5 | 55.9 | 56.3 | 56.6 | 56.9 | 57.2 | CF | Cathaleen’s Fall | 0.964 | 16.5 | 16.8 | 16.6 | 16.4 | 16.4 | 16.4 | 16.4 | 16.5 | 16.6 | 16.7 | CF | Cathaleens Fall | 0.999 | 6.4 | 6.4 | 6.4 | 6.4 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
CF | Cathaleen’s Fall | 0.998 | 21.4 | 21.8 | 21.7 | 21.8 | 21.8 | 21.9 | 22 | 22.2 | 22.4 | 22.6 | CFM | Castlefarm | 0.95 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | CFM | Castlefarm | 0.95 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8
CFM | Castlefarm | 0.95 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | CHA | Charleville | 0.96 | 16.1 | 16.4 | 16.2 | 16 | 16 | 16 | 16 | 16.1 | 16.2 | 16.3 | CHA | Charleville | 0.999 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
CHA | Charleville | 0.988 | 20.8 | 21.3 | 21.2 | 21.2 | 21.3 | 21.3 | 21.4 | 21.6 | 21.9 | 22 | CKM | Carrickmines | 0.998 | 291.8 | 296.1 | 294.2 | 291 | 290.2 | 290.1 | 290.8 | 292.2 | 294.1 | 295.1 | CKM | Carrickmines | 0.998 | 144.3 | 144.2 | 143.9 | 143.8 | 143.6 | 143.5 | 143.4 | 143.3 | 143.2 | 143.2
CKM | Carrickmines | 0.998 | 362.6 | 369.3 | 367.3 | 368.4 | 368.8 | 369.8 | 371.7 | 374.3 | 378.1 | 380 | CLE | Clonee | 0.95 | 71.8 | 83.2 | 94.6 | 106 | 117.4 | 128.8 | 135.4 | 135.4 | 135.4 | 135.4 | CLE | Clonee | 0.95 | 86.5 | 105.5 | 124.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5
CLE | Clonee | 0.95 | 86.5 | 105.5 | 124.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | CLG | Cloghran | 0.95 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | CLG | Cloghran | 0.95 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7
CLG | Cloghran | 0.95 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | 81.7 | CLN | Cloon | 0.925 | 21.1 | 21.5 | 21.4 | 21.1 | 21 | 21 | 21.1 | 21.2 | 21.3 | 21.4 | CLN | Cloon | 1 | 7.1 | 7.1 | 7.1 | 7 | 7 | 7 | 7 | 7 | 7 | 7
CLN | Cloon | 1 | 27.4 | 28 | 27.8 | 27.9 | 27.9 | 28 | 28.2 | 28.4 | 28.8 | 28.9 | CLU | Clutterland | 0.95 | 0 | 3.8 | 3.8 | 9.5 | 14.3 | 20 | 24.7 | 30.4 | 35.2 | 40.9 | CLU | Clutterland | 0.95 | 0 | 3.8 | 3.8 | 9.5 | 14.3 | 20 | 24.7 | 30.4 | 35.2 | 40.9
CLU | Clutterland | 0.95 | 0 | 3.8 | 3.8 | 9.5 | 14.3 | 20 | 24.7 | 30.4 | 35.2 | 40.9 | CLW | Carlow | 0.991 | 55.3 | 56.3 | 55.8 | 55.1 | 54.9 | 54.9 | 55 | 55.4 | 55.8 | 56 | CLW | Carlow | 0.982 | 18.2 | 18.2 | 18.2 | 18.1 | 18.1 | 18.1 | 18.1 | 18 | 18 | 18
CLW | Carlow | 0.992 | 71.6 | 73.2 | 72.7 | 72.9 | 73 | 73.3 | 73.7 | 74.3 | 75.2 | 75.6 | COL | College Park | 0.986 | 26.5 | 27 | 26.7 | 26.4 | 26.3 | 26.3 | 26.4 | 26.5 | 26.7 | 26.8 | COL | College Park | 0.993 | 21.1 | 21.1 | 21.1 | 21 | 21 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9
COL | College Park | 0.994 | 34.3 | 35 | 34.8 | 35 | 35 | 35.1 | 35.3 | 35.6 | 36 | 36.2 | COL (N) | Coleraine | 0.99 | 12.5 | 12.8 | 12.6 | 12.9 | 13 | 13 | 13.1 | 13.2 | 13.3 | 13.3 | COL (N) | Coleraine | 0.99 | 12.5 | 12.8 | 12.6 | 12.9 | 13 | 13 | 13.1 | 13.2 | 13.3 | 13.3
COL (N) | Coleraine | 0.99 | 42.8 | 43.5 | 43.1 | 44 | 44.3 | 44.5 | 44.7 | 45 | 45.2 | 45.5 | COS | Carrick on Shannon | 0.989 | 23 | 23.4 | 23.2 | 22.9 | 22.8 | 22.8 | 22.9 | 23 | 23.2 | 23.3 | COS | Carrick on Shannon | 1 | 8 | 8 | 8 | 8 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9
COS | Carrick-On-Shanon | 0.996 | 29.7 | 30.4 | 30.2 | 30.3 | 30.3 | 30.4 | 30.6 | 30.9 | 31.2 | 31.4 | COW | Cow Cross | 0.997 | 13.4 | 13.6 | 13.5 | 13.3 | 13.3 | 13.3 | 13.3 | 13.4 | 13.5 | 13.6 | COW | Cow Cross | 1 | 8.2 | 8.2 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1
COW | Cow Cross | 1 | 17.3 | 17.7 | 17.6 | 17.7 | 17.7 | 17.7 | 17.9 | 18 | 18.2 | 18.3 | CPS | Coolkeeragh | 0.99 | 7.4 | 7.6 | 7.5 | 7.7 | 7.7 | 7.8 | 7.8 | 7.8 | 7.9 | 7.9 | CPS | Coolkeeragh | 0.99 | 7.4 | 7.6 | 7.5 | 7.7 | 7.7 | 7.8 | 7.8 | 7.8 | 7.9 | 7.9
CPS | Coolkeeragh | 0.99 | 25.4 | 25.8 | 25.6 | 26.1 | 26.3 | 26.4 | 26.6 | 26.7 | 26.9 | 27 | CRA | Crane | 0.979 | 25.1 | 25.6 | 25.4 | 25.1 | 25 | 25 | 25 | 25.2 | 25.4 | 25.5 | CRA | Crane | 0.999 | 12 | 12 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.8 | 11.8
CRA | Crane | 0.992 | 32.6 | 33.3 | 33.1 | 33.2 | 33.2 | 33.3 | 33.5 | 33.8 | 34.2 | 34.4 | CRE | Cregagh | 0.99 | 25.2 | 21.2 | 21.1 | 21.6 | 21.7 | 21.9 | 22 | 22.1 | 22.3 | 22.4 | CRE | Cregagh | 0.99 | 25.2 | 21.2 | 21.1 | 21.6 | 21.7 | 21.9 | 22 | 22.1 | 22.3 | 22.4
CRE | Cregagh | 0.99 | 86.2 | 72.5 | 71.9 | 73.6 | 74.2 | 74.7 | 75.2 | 75.6 | 76 | 76.5 | CRG | Creagh | 0.99 | 7.3 | 7.4 | 7.4 | 7.5 | 7.6 | 7.6 | 7.6 | 7.7 | 7.7 | 7.8 | CRG | Creagh | 0.99 | 7.3 | 7.4 | 7.4 | 7.5 | 7.6 | 7.6 | 7.6 | 7.7 | 7.7 | 7.8
CRG | Creagh | 0.99 | 24.9 | 25.3 | 25.1 | 25.6 | 25.8 | 25.9 | 26.1 | 26.2 | 26.3 | 26.5 | CRH | Cruiserath | 0.95 | 3.8 | 9 | 14.3 | 19.5 | 24.7 | 29.9 | 35.2 | 40.4 | 45.6 | 50.8 | CRH | Cruiserath | 0.95 | 3.8 | 9 | 14.3 | 19.5 | 24.7 | 29.9 | 35.2 | 40.4 | 45.6 | 50.8
CRH | Cruiserath | 0.95 | 3.8 | 9 | 14.3 | 19.5 | 24.7 | 29.9 | 35.2 | 40.4 | 45.6 | 50.8 | CRO | Coolroe | 1 | 8.4 | 8.6 | 8.5 | 8.4 | 8.4 | 8.4 | 8.4 | 8.5 | 8.5 | 8.6 | CRO | Coolroe | 1 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.6
CRO | Coolroe | 1 | 10.9 | 11.2 | 11.1 | 11.1 | 11.2 | 11.2 | 11.3 | 11.3 | 11.5 | 11.5 | CVW | Castleview | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8 | CVW | Castleview | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8
CVW | Castleview | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8 | CVW | Castleview | 0.982 | 25.9 | 26.3 | 26.1 | 25.8 | 25.7 | 25.7 | 25.8 | 25.9 | 26.1 | 26.2 | CVW | Castleview | 0.992 | 14.9 | 14.9 | 14.9 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8
CVW | Castleview | 0.989 | 33.5 | 34.2 | 34 | 34.1 | 34.2 | 34.3 | 34.5 | 34.8 | 35.2 | 35.4 | DAL | Dallow | 0.987 | 14.8 | 15.1 | 15 | 14.8 | 14.7 | 14.7 | 14.8 | 14.9 | 15 | 15 | DAL | Dallow | 0.993 | 4.8 | 4.8 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7
DAL | Dallow | 0.981 | 19.2 | 19.6 | 19.5 | 19.6 | 19.6 | 19.7 | 19.8 | 19.9 | 20.2 | 20.3 | DDK | Dundalk | 0.986 | 52.6 | 53.5 | 53.1 | 52.4 | 52.2 | 52.2 | 52.4 | 52.7 | 53.1 | 53.3 | DDK | Dundalk | 1 | 18.3 | 18.3 | 18.3 | 18.2 | 18.2 | 18.2 | 18.1 | 18.1 | 18.1 | 18.1
DDK | Dundalk | 0.99 | 68.1 | 69.6 | 69.1 | 69.4 | 69.5 | 69.7 | 70.1 | 70.7 | 71.5 | 72 | DFR | Dunfirth | 0.991 | 8.6 | 8.7 | 8.7 | 8.6 | 8.5 | 8.5 | 8.5 | 8.6 | 8.7 | 8.7 | DFR | Dunfirth | 1 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2
DFR | Dunfirth | 0.96 | 11.1 | 11.4 | 11.3 | 11.3 | 11.3 | 11.4 | 11.4 | 11.5 | 11.7 | 11.7 | DGN | Dungarvan | 0.984 | 39 | 39.7 | 39.4 | 38.9 | 38.7 | 38.7 | 38.8 | 39.1 | 39.4 | 39.5 | DGN | Dungarvan | 1 | 15.1 | 15.1 | 15.1 | 15 | 15 | 15 | 15 | 15 | 14.9 | 14.9
DGN | Dungarvan | 0.991 | 50.5 | 51.6 | 51.3 | 51.5 | 51.5 | 51.7 | 52 | 52.4 | 53.1 | 53.4 | DLT | Dalton | 0.981 | 22.6 | 23 | 22.8 | 22.5 | 22.5 | 22.5 | 22.5 | 22.7 | 22.8 | 22.9 | DLT | Dalton | 0.999 | 10.7 | 10.7 | 10.7 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6
DLT | Dalton | 0.99 | 29.3 | 29.9 | 29.7 | 29.9 | 29.9 | 30 | 30.2 | 30.4 | 30.8 | 31 | DMY | Dunmanway | 0.976 | 27.6 | 28.1 | 27.8 | 27.5 | 27.4 | 27.4 | 27.4 | 27.6 | 27.8 | 27.9 | DMY | Dunmanway | 0.983 | 10.1 | 10.1 | 10.1 | 10 | 10 | 10 | 10 | 10 | 10 | 10
DMY | Dunmanway | 0.991 | 35.7 | 36.5 | 36.2 | 36.4 | 36.4 | 36.5 | 36.8 | 37 | 37.5 | 37.7 | DON | Donegall | 0.99 | 26.8 | 26.8 | 26.1 | 26.2 | 26 | 25.7 | 25.4 | 25.5 | 25.7 | 25.8 | DON | Donegall | 0.99 | 26.8 | 26.8 | 26.1 | 26.2 | 26 | 25.7 | 25.4 | 25.5 | 25.7 | 25.8
DON | Donegall | 0.99 | 91.4 | 91.5 | 89.1 | 89.5 | 88.6 | 87.7 | 86.7 | 87.2 | 87.6 | 88.1 | DOO | Doon | 0.984 | 21.9 | 22.3 | 22.1 | 21.9 | 21.8 | 21.8 | 21.8 | 22 | 22.1 | 22.2 | DOO | Doon | 1 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
DOO | Doon | 0.991 | 28.4 | 29 | 28.8 | 28.9 | 29 | 29.1 | 29.2 | 29.5 | 29.8 | 30 | DRU | Drumline | 0.945 | 24.4 | 24.9 | 24.7 | 24.3 | 24.2 | 24.2 | 24.3 | 24.5 | 24.6 | 24.7 | DRU | Drumline | 0.873 | 12.9 | 12.9 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.7 | 12.7
DRU | Drumline | 0.952 | 31.6 | 32.3 | 32.1 | 32.2 | 32.3 | 32.4 | 32.6 | 32.8 | 33.2 | 33.4 | DRU (N) | Drumnakelly | 0.98 | 26.8 | 27.4 | 27.1 | 27.7 | 27.9 | 28.1 | 28.3 | 28.4 | 28.6 | 28.7 | DRU (N) | Drumnakelly | 0.98 | 26.8 | 27.4 | 27.1 | 27.7 | 27.9 | 28.1 | 28.3 | 28.4 | 28.6 | 28.7
DRU (N) | Drumnakelly | 0.98 | 91.7 | 93.4 | 92.5 | 94.6 | 95.2 | 95.9 | 96.4 | 97 | 97.5 | 98.1 | DRY | Drybridge | 0.985 | 71.4 | 72.7 | 72.1 | 71.1 | 70.9 | 70.9 | 71.1 | 71.5 | 72.1 | 72.4 | DRY | Drybridge | 1 | 24.3 | 24.3 | 24.2 | 24.2 | 24.1 | 24.1 | 24.1 | 24.1 | 24 | 24
DRY | Drybridge | 0.994 | 92.5 | 94.5 | 93.9 | 94.2 | 94.3 | 94.6 | 95.2 | 96 | 97.1 | 97.7 | DUN | Dungannon | 0.99 | 28.4 | 28.9 | 28.7 | 29.3 | 29.5 | 29.7 | 29.8 | 29.9 | 30.1 | 30.3 | DUN | Dungannon | 0.99 | 28.4 | 28.9 | 28.7 | 29.3 | 29.5 | 29.7 | 29.8 | 29.9 | 30.1 | 30.3
DUN | Dungannon | 0.99 | 97 | 98.8 | 97.9 | 100 | 100.6 | 101.2 | 101.7 | 102.2 | 102.8 | 103.4 | EDE | Eden | 0.98 | 10.1 | 10.3 | 10.2 | 10.4 | 10.5 | 10.6 | 10.6 | 10.7 | 10.7 | 10.8 | EDE | Eden | 0.98 | 10.1 | 10.3 | 10.2 | 10.4 | 10.5 | 10.6 | 10.6 | 10.7 | 10.7 | 10.8
EDE | Eden | 0.98 | 34.6 | 35.2 | 34.9 | 35.7 | 35.9 | 36.1 | 36.2 | 36.4 | 36.6 | 36.9 | ENN | Ennis | 0.981 | 49.1 | 50 | 49.6 | 48.9 | 48.8 | 48.7 | 48.9 | 49.2 | 49.6 | 49.8 | ENN | Ennis | 0.996 | 22 | 22 | 21.9 | 21.9 | 21.9 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8
ENN | Ennis | 0.986 | 63.6 | 65 | 64.6 | 64.8 | 64.9 | 65.1 | 65.5 | 66 | 66.8 | 67.2 | ENN (N) | Enniskillen | 0.99 | 16.6 | 16.9 | 16.8 | 17.2 | 17.2 | 17.4 | 17.4 | 17.5 | 17.6 | 17.7 | ENN (N) | Enniskillen | 0.99 | 16.6 | 16.9 | 16.8 | 17.2 | 17.2 | 17.4 | 17.4 | 17.5 | 17.6 | 17.7
ENN (N) | Enniskillen | 0.99 | 56.8 | 57.8 | 57.3 | 58.6 | 58.9 | 59.2 | 59.5 | 59.8 | 60.2 | 60.5 | FIN (I) | Finglas | 0.994 | 378.5 | 384.8 | 381.9 | 377.4 | 376.2 | 375.9 | 377.1 | 379.1 | 381.8 | 383.2 | FIN (I) | Finglas | 0.993 | 184.9 | 184.7 | 184.4 | 184.1 | 183.9 | 183.7 | 183.5 | 183.4 | 183.2 | 183.1
FIN (I) | Finglas | 0.984 | 480.8 | 490.5 | 487.6 | 489.2 | 489.8 | 491.3 | 494 | 497.7 | 503.2 | 506.1 | FIN (N) | Finaghy | 0.99 | 9.1 | 9.2 | 9.2 | 9.4 | 9.4 | 9.5 | 9.5 | 9.6 | 9.6 | 9.7 | FIN (N) | Finaghy | 0.99 | 9.1 | 9.2 | 9.2 | 9.4 | 9.4 | 9.5 | 9.5 | 9.6 | 9.6 | 9.7
FIN (N) | Finaghy | 0.99 | 31 | 31.5 | 31.2 | 31.9 | 32.1 | 32.3 | 32.4 | 32.6 | 32.8 | 33 | FTT | Fortunestown | 0.997 | 11.1 | 11.3 | 11.2 | 11 | 11 | 11 | 11 | 11.1 | 11.2 | 11.2 | FTT | Fortunestown | 1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1
FTT | Fortunestown | 0.998 | 14.4 | 14.7 | 14.6 | 14.6 | 14.6 | 14.7 | 14.8 | 14.9 | 15.1 | 15.2 | GAL | Galway | 0.988 | 75.5 | 76.9 | 76.3 | 75.3 | 75 | 75 | 75.2 | 75.7 | 76.3 | 76.6 | GAL | Galway | 1 | 34.2 | 34.1 | 34.1 | 34 | 33.9 | 33.9 | 33.9 | 33.8 | 33.8 | 33.8
GAL | Galway | 0.994 | 97.9 | 100 | 99.3 | 99.7 | 99.8 | 100.1 | 100.7 | 101.5 | 102.7 | 103.4 | GI | Great Island | 0.952 | 12.8 | 13 | 12.9 | 12.7 | 12.7 | 12.7 | 12.7 | 12.8 | 12.9 | 12.9 | GI | Great Island | 0.979 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
GI | Great Island | 0.964 | 16.5 | 16.9 | 16.8 | 16.8 | 16.9 | 16.9 | 17 | 17.1 | 17.3 | 17.5 | GIL | Gilra | 0.95 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | GIL | Gilra | 0.95 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4
GIL | Gilra | 0.95 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | GLE | Glenlara | 0.998 | 13.7 | 13.9 | 13.8 | 13.6 | 13.6 | 13.6 | 13.6 | 13.7 | 13.8 | 13.9 | GLE | Glenlara | 0.956 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
GLE | Glenlara | 0.994 | 17.7 | 18.1 | 18 | 18.1 | 18.1 | 18.2 | 18.3 | 18.4 | 18.6 | 18.7 | GLE (N) | Glengormley | 0.97 | 9.2 | 9.3 | 9.2 | 9.4 | 9.4 | 9.4 | 9.4 | 9.5 | 9.5 | 9.6 | GLE (N) | Glengormley | 0.97 | 9.2 | 9.3 | 9.2 | 9.4 | 9.4 | 9.4 | 9.4 | 9.5 | 9.5 | 9.6
GLE (N) | Glengormley | 0.98 | 31.4 | 31.8 | 31.4 | 32 | 32.1 | 32.1 | 32.2 | 32.3 | 32.5 | 32.7 | GRI | Griffinrath | 0.997 | 51.6 | 52.5 | 52.1 | 51.4 | 51.2 | 51.2 | 51.4 | 51.7 | 52.1 | 52.3 | GRI | Griffinrath | 1 | 23.1 | 23 | 23 | 22.9 | 22.9 | 22.9 | 22.8 | 22.8 | 22.8 | 22.8
GRI | Griffinrath | 0.994 | 66.8 | 68.3 | 67.8 | 68.1 | 68.1 | 68.4 | 68.8 | 69.3 | 70.1 | 70.6 | GWE | Gortawee | 0.98 | 8.5 | 8.7 | 8.6 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.6 | 8.6 | GWE | Gortawee | 0.981 | 6.5 | 6.5 | 6.5 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
GWE | Gortawee | 0.991 | 11 | 11.3 | 11.2 | 11.2 | 11.3 | 11.3 | 11.4 | 11.4 | 11.6 | 11.7 | GWE | Gortawee | 0.95 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | GWE | Gortawee | 0.95 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
GWE | Gortawee | 0.95 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | IKE | Ikerrin | 0.967 | 24.5 | 25 | 24.8 | 24.4 | 24.4 | 24.3 | 24.4 | 24.6 | 24.8 | 24.9 | IKE | Ikerrin | 0.996 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
IKE | Ikerrin | 0.981 | 31.8 | 32.5 | 32.3 | 32.4 | 32.4 | 32.5 | 32.7 | 33 | 33.4 | 33.6 | INC | Inchicore | 0.995 | 420.6 | 449.8 | 475.9 | 500.4 | 517.6 | 534.9 | 553.7 | 571 | 590.7 | 606.9 | INC | Inchicore | 0.984 | 307.5 | 332.3 | 360.1 | 387.3 | 405.2 | 422.5 | 440.5 | 456.2 | 473.9 | 489.2
INC | Inchicor | 0.999 | 489 | 520.5 | 546.6 | 575.2 | 593.9 | 612 | 631.9 | 650.3 | 671.8 | 689 | KBY | Kilbarry | 0.993 | 67.9 | 69.2 | 68.6 | 67.7 | 67.5 | 67.5 | 67.7 | 68.1 | 68.6 | 68.9 | KBY | Kilbarry | 1 | 20.3 | 20.3 | 20.2 | 20.2 | 20.2 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1
KBY | Kilbarry | 0.991 | 88 | 89.9 | 89.4 | 89.7 | 89.8 | 90.1 | 90.6 | 91.3 | 92.4 | 93 | KCY | Kilcarbery | 0.95 | 0 | 0 | 0 | 4.8 | 9.5 | 14.3 | 19 | 23.8 | 23.8 | 23.8 | KCY | Kilcarbery | 0.95 | 0 | 0 | 0 | 4.8 | 9.5 | 14.3 | 19 | 23.8 | 23.8 | 23.8
KCY | Kilcarbery | 0.95 | 0 | 0 | 0 | 4.8 | 9.5 | 14.3 | 19 | 23.8 | 23.8 | 23.8 | KER | Knockearagh | 0.971 | 31.9 | 32.4 | 32.2 | 31.8 | 31.6 | 31.6 | 31.7 | 31.9 | 32.2 | 32.3 | KER | Knockearagh | 0.99 | 15.3 | 15.3 | 15.3 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.1 | 15.1
KER | Knockearagh | 0.981 | 41.3 | 42.2 | 41.9 | 42 | 42.1 | 42.2 | 42.5 | 42.8 | 43.3 | 43.6 | KGE | Kishoge | 0.95 | 0 | 0 | 0 | 4.8 | 9.5 | 14.3 | 19 | 23.8 | 23.8 | 23.8 | KGE | Kishoge | 0.95 | 0 | 0 | 0 | 4.8 | 9.5 | 14.3 | 19 | 23.8 | 23.8 | 23.8
KGE | Kishoge | 0.95 | 0 | 0 | 0 | 4.8 | 9.5 | 14.3 | 19 | 23.8 | 23.8 | 23.8 | KIL | Kilteel | 0.988 | 28 | 28.5 | 28.3 | 27.9 | 27.8 | 27.8 | 27.9 | 28 | 28.3 | 28.4 | KIL | Kilteel | 0.998 | 9.8 | 9.8 | 9.8 | 9.8 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7
KIL | Kilteel | 0.97 | 36.3 | 37 | 36.8 | 36.9 | 37 | 37.1 | 37.3 | 37.6 | 38.1 | 38.3 | KIN | Kinnegad | 0.95 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | KIN | Kinnegad | 0.95 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2
KIN | Kinnegad | 0.95 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | KKY | Kilkenny | 0.978 | 47.6 | 48.5 | 48.1 | 47.5 | 47.3 | 47.3 | 47.4 | 47.7 | 48.1 | 48.3 | KKY | Kilkenny | 1 | 19 | 18.9 | 18.9 | 18.9 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.7
KKY | Kilkenny | 0.988 | 61.7 | 63 | 62.6 | 62.9 | 62.9 | 63.1 | 63.5 | 64 | 64.8 | 65.2 | KLM | Kilmore | 0.989 | 15.5 | 15.8 | 15.7 | 15.4 | 15.4 | 15.4 | 15.4 | 15.5 | 15.6 | 15.7 | KLM | Kilmore | 0.992 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.3 | 9.3 | 9.3 | 9.3
KLM | Kilmore | 0.99 | 20.1 | 20.5 | 20.4 | 20.5 | 20.5 | 20.5 | 20.7 | 20.8 | 21.1 | 21.2 | KNO | Knock | 0.99 | 15 | 13.4 | 13.3 | 13.5 | 13.6 | 13.7 | 13.8 | 13.9 | 14 | 14 | KNO | Knock | 0.99 | 15 | 13.4 | 13.3 | 13.5 | 13.6 | 13.7 | 13.8 | 13.9 | 14 | 14
KNO | Knock | 0.99 | 51.3 | 45.6 | 45.2 | 46.2 | 46.6 | 46.9 | 47.1 | 47.4 | 47.6 | 47.9 | KTN | Killoteran | 0.976 | 11.2 | 11.5 | 11.4 | 11.2 | 11.2 | 11.2 | 11.2 | 11.3 | 11.4 | 11.4 | KTN | Killoteran | 0.993 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
KTN | Killoteran | 0.982 | 14.6 | 14.9 | 14.8 | 14.8 | 14.9 | 14.9 | 15 | 15.1 | 15.3 | 15.4 | KUR | Knockumber | 0.95 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | KUR | Knockumber | 0.95 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7
KUR | Knockumber | 0.95 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | KYT | Kellystown | 0.95 | 28.5 | 59.9 | 114 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | KYT | Kellystown | 0.95 | 28.5 | 59.9 | 114 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9
KYT | Kellystown | 0.95 | 28.5 | 59.9 | 114 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | LA | Lanesborough | 0.984 | 13.2 | 13.5 | 13.4 | 13.2 | 13.1 | 13.1 | 13.2 | 13.3 | 13.4 | 13.4 | LA | Lanesborough | 1 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6
LA | Lanesborough | 0.989 | 17.1 | 17.5 | 17.4 | 17.5 | 17.5 | 17.5 | 17.7 | 17.8 | 18 | 18.1 | LAR | Larne | 0.99 | 8.4 | 8.6 | 8.5 | 8.6 | 8.7 | 8.7 | 8.8 | 8.8 | 8.9 | 8.9 | LAR | Larne | 0.99 | 8.4 | 8.6 | 8.5 | 8.6 | 8.7 | 8.7 | 8.8 | 8.8 | 8.9 | 8.9
LAR | Larne | 0.99 | 28.7 | 29.2 | 28.9 | 29.5 | 29.7 | 29.8 | 30 | 30.1 | 30.3 | 30.5 | LET | Letterkenny | 0.985 | 50.6 | 51.5 | 51.1 | 50.4 | 50.3 | 50.2 | 50.4 | 50.7 | 51.1 | 51.3 | LET | Letterkenny | 0.996 | 17.8 | 17.8 | 17.8 | 17.7 | 17.7 | 17.7 | 17.7 | 17.6 | 17.6 | 17.6
LET | Letterkenny | 0.991 | 65.6 | 67 | 66.58 | 66.81 | 66.9 | 67.12 | 67.52 | 68.06 | 68.86 | 69.28 | LIB | Liberty Street | 0.986 | 19.9 | 20.2 | 20.1 | 19.8 | 19.7 | 19.7 | 19.8 | 19.9 | 20.1 | 20.2 | LIB | Liberty Street | 0.989 | 7.9 | 7.9 | 7.9 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8
LIB | Liberty Street | 0.994 | 25.8 | 26.3 | 26.1 | 26.2 | 26.3 | 26.4 | 26.5 | 26.7 | 27 | 27.2 | LIM | Limerick | 0.993 | 66.8 | 68 | 67.5 | 66.6 | 66.4 | 66.3 | 66.5 | 66.9 | 67.4 | 67.7 | LIM | Limerick | 1 | 30.2 | 30.1 | 30.1 | 30 | 30 | 29.9 | 29.9 | 29.9 | 29.9 | 29.8
LIM | Limerick | 0.995 | 86.5 | 88.4 | 87.9 | 88.2 | 88.3 | 88.6 | 89.1 | 89.8 | 90.9 | 91.4 | LIM (N) | Limavady | 0.99 | 7.3 | 7.4 | 7.3 | 7.5 | 7.5 | 7.6 | 7.6 | 7.6 | 7.7 | 7.7 | LIM (N) | Limavady | 0.99 | 7.3 | 7.4 | 7.3 | 7.5 | 7.5 | 7.6 | 7.6 | 7.6 | 7.7 | 7.7
LIM (N) | Limavady | 0.99 | 24.8 | 25.2 | 25 | 25.5 | 25.6 | 25.8 | 25.9 | 26 | 26.2 | 26.3 | LIS | Lisdrum | 0.952 | 24.8 | 25.3 | 25.1 | 24.7 | 24.7 | 24.6 | 24.7 | 24.9 | 25.1 | 25.2 | LIS | Lisdrum | 0.992 | 9.8 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.6
LIS | Lisdrum | 0.975 | 32.2 | 32.8 | 32.6 | 32.8 | 32.8 | 32.9 | 33.1 | 33.4 | 33.8 | 34 | LIS (N) | Lisburn | 0.99 | 21.7 | 22.1 | 21.9 | 22.4 | 22.5 | 22.6 | 22.7 | 22.9 | 23 | 23.1 | LIS (N) | Lisburn | 0.99 | 21.7 | 22.1 | 21.9 | 22.4 | 22.5 | 22.6 | 22.7 | 22.9 | 23 | 23.1
LIS (N) | Lisburn | 0.99 | 74 | 75.4 | 74.7 | 76.3 | 76.8 | 77.2 | 77.6 | 78 | 78.5 | 78.9 | LMR | Lisaghmore | 0.98 | 9.6 | 9.8 | 9.7 | 9.9 | 10 | 10 | 10.1 | 10.1 | 10.2 | 10.3 | LMR | Lisaghmore | 0.98 | 9.6 | 9.8 | 9.7 | 9.9 | 10 | 10 | 10.1 | 10.1 | 10.2 | 10.3
LMR | Lisaghmore | 0.98 | 32.9 | 33.5 | 33.2 | 33.9 | 34.1 | 34.3 | 34.4 | 34.6 | 34.8 | 35 | LOG | Loguestown | 0.98 | 11.4 | 11.6 | 11.5 | 11.8 | 11.8 | 11.9 | 12 | 12 | 12.1 | 12.2 | LOG | Loguestown | 0.98 | 11.4 | 11.6 | 11.5 | 11.8 | 11.8 | 11.9 | 12 | 12 | 12.1 | 12.2
LOG | Loguestown | 0.98 | 39 | 39.7 | 39.4 | 40.2 | 40.4 | 40.7 | 40.8 | 41.1 | 41.3 | 41.5 | MAC | Macroom | 0.973 | 13.9 | 14.1 | 14 | 13.8 | 13.8 | 13.8 | 13.8 | 13.9 | 14 | 14.1 | MAC | Macroom | 0.96 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7 | 7 | 7 | 7 | 7
MAC | Macroom | 0.994 | 18 | 18.4 | 18.2 | 18.3 | 18.3 | 18.4 | 18.5 | 18.7 | 18.9 | 19 | MAL | Mallow | 0.981 | 19.1 | 19.4 | 19.3 | 19 | 18.9 | 18.9 | 19 | 19.1 | 19.3 | 19.3 | MAL | Mallow | 0.988 | 12.9 | 12.9 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.7 | 12.7
MAL | Mallow | 0.989 | 24.7 | 25.2 | 25.1 | 25.2 | 25.2 | 25.3 | 25.4 | 25.6 | 25.9 | 26.1 | MCE | Mace IBM | 0.95 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | MCE | Mace | 0.95 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6
MCE | Mace | 0.95 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | MCE | Macetown | 0.995 | 24.2 | 24.7 | 24.5 | 24.1 | 24.1 | 24 | 24.1 | 24.3 | 24.5 | 24.5 | MCE | Macetown | 0.95 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1
MCE | Macetown | 0.997 | 31.4 | 32.1 | 31.9 | 32 | 32 | 32.1 | 32.3 | 32.6 | 32.9 | 33.1 | MID | Midleton | 0.98 | 34.4 | 35.1 | 34.8 | 34.3 | 34.2 | 34.2 | 34.3 | 34.5 | 34.8 | 34.9 | MID | Midleton | 0.99 | 21.2 | 21.1 | 21.1 | 21 | 21 | 21 | 21 | 20.9 | 20.9 | 20.9
MID | Midleton | 0.985 | 44.6 | 45.6 | 45.3 | 45.5 | 45.5 | 45.7 | 45.9 | 46.3 | 46.9 | 47.1 | MLN | Mullagharlin | 0.95 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | MLN | Mullagharlin | 0.95 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
MLN | Mullagharlin | 0.95 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | MON | Monread | 0.975 | 11.1 | 11.3 | 11.2 | 11 | 11 | 11 | 11 | 11.1 | 11.2 | 11.2 | MON | Monread | 0.999 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
MON | Monread | 0.992 | 14.4 | 14.7 | 14.6 | 14.6 | 14.6 | 14.7 | 14.8 | 14.9 | 15.1 | 15.2 | MOY | Moy | 0.989 | 24.2 | 24.6 | 24.4 | 24.1 | 24 | 24 | 24.1 | 24.2 | 24.4 | 24.5 | MOY | Moy | 1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10 | 10 | 10 | 10
MOY | Moy | 0.993 | 31.3 | 32 | 31.8 | 31.9 | 31.9 | 32 | 32.2 | 32.5 | 32.9 | 33.1 | MR | Marina | 0.992 | 13.5 | 13.7 | 13.6 | 13.4 | 13.4 | 13.4 | 13.4 | 13.5 | 13.6 | 13.7 | MR | Marina | 0.999 | 4.8 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7
MR | Marina | 0.996 | 17.5 | 17.9 | 17.7 | 17.8 | 17.8 | 17.9 | 18 | 18.1 | 18.4 | 18.5 | MTH | Meath Hill | 0.938 | 45.2 | 46 | 45.6 | 45 | 44.8 | 44.8 | 45 | 45.2 | 45.6 | 45.8 | MTH | Meath Hill | 0.984 | 13.5 | 13.5 | 13.5 | 13.5 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
MTH | Meath Hill | 0.96 | 58.5 | 59.8 | 59.4 | 59.6 | 59.7 | 59.9 | 60.2 | 60.7 | 61.4 | 61.8 | MUL | Mullingar | 0.985 | 35.7 | 36.4 | 36.1 | 35.6 | 35.5 | 35.5 | 35.6 | 35.8 | 36.1 | 36.2 | MUL | Mullingar | 0.998 | 13.1 | 13.1 | 13.1 | 13 | 13 | 13 | 13 | 13 | 13 | 13
MUL | Mullingar | 0.989 | 46.3 | 47.3 | 47 | 47.1 | 47.2 | 47.4 | 47.6 | 48 | 48.6 | 48.9 | MUN | Mungret | 0.95 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | MUN | Mungret | 0.95 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5
MUN | Mungret | 0.95 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | NAR | Newtownards | 0.99 | 13.3 | 13.5 | 13.4 | 13.7 | 13.8 | 13.8 | 13.9 | 14 | 14.1 | 14.1 | NAR | Newtownards | 0.99 | 13.3 | 13.5 | 13.4 | 13.7 | 13.8 | 13.8 | 13.9 | 14 | 14.1 | 14.1
NAR | Newtownards | 0.99 | 45.4 | 46.2 | 45.8 | 46.7 | 47 | 47.3 | 47.5 | 47.7 | 48 | 48.3 | NAV | Navan | 0.98 | 49.6 | 50.5 | 50.1 | 49.5 | 49.3 | 49.3 | 49.4 | 49.7 | 50.1 | 50.3 | NAV | Navan | 0.969 | 17.7 | 17.7 | 17.6 | 17.6 | 17.6 | 17.6 | 17.5 | 17.5 | 17.5 | 17.5
NAV | Navan | 0.987 | 64.3 | 65.7 | 65.3 | 65.5 | 65.6 | 65.8 | 66.2 | 66.7 | 67.5 | 67.9 | NEW | Newbridge | 0.981 | 33.5 | 34.1 | 33.9 | 33.4 | 33.3 | 33.3 | 33.4 | 33.6 | 33.8 | 34 | NEW | Newbridge | 1 | 13.2 | 13.2 | 13.2 | 13.2 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1
NEW | Newbridge | 0.991 | 43.4 | 44.4 | 44.1 | 44.2 | 44.3 | 44.4 | 44.7 | 45.1 | 45.6 | 45.9 | NEW (N) | Newry | 0.99 | 23.4 | 23.9 | 23.7 | 24.2 | 24.3 | 24.5 | 24.6 | 24.7 | 24.8 | 25 | NEW (N) | Newry | 0.99 | 23.4 | 23.9 | 23.7 | 24.2 | 24.3 | 24.5 | 24.6 | 24.7 | 24.8 | 25
NEW (N) | Newry | 0.99 | 80 | 81.5 | 80.7 | 82.5 | 83 | 83.5 | 83.9 | 84.3 | 84.8 | 85.3 | NNA | Nenagh | 0.954 | 17.8 | 18.1 | 18 | 17.7 | 17.7 | 17.7 | 17.7 | 17.8 | 18 | 18 | NNA | Nenagh | 0.977 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1
NNA | Nenagh | 0.947 | 23 | 23.5 | 23.4 | 23.5 | 23.5 | 23.6 | 23.7 | 23.9 | 24.2 | 24.3 | ODE | Oldbridge | 0.95 | 0 | 0 | 3.8 | 9.5 | 14.3 | 20 | 24.7 | 30.4 | 35.2 | 40.9 | ODE | Oldbridge | 0.95 | 0 | 0 | 3.8 | 9.5 | 14.3 | 20 | 24.7 | 30.4 | 35.2 | 40.9
ODE | Oldbridge | 0.95 | 0 | 0 | 3.8 | 9.5 | 14.3 | 20 | 24.7 | 30.4 | 35.2 | 40.9 | OLD | Oldcourt | 0.95 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | OLD | Oldcourt | 0.95 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OLD | Oldcourt | 0.95 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | OMA | Omagh | 0.99 | 17.8 | 18.1 | 17.9 | 18.3 | 18.4 | 18.5 | 18.6 | 18.7 | 18.8 | 18.9 | OMA | Omagh | 0.99 | 17.8 | 18.1 | 17.9 | 18.3 | 18.4 | 18.5 | 18.6 | 18.7 | 18.8 | 18.9
OMA | Omagh | 0.99 | 60.7 | 61.8 | 61.2 | 62.5 | 62.8 | 63.2 | 63.5 | 63.8 | 64.2 | 64.5 | OUG | Oughtragh | 0.992 | 21.3 | 21.7 | 21.5 | 21.2 | 21.1 | 21.1 | 21.2 | 21.3 | 21.5 | 21.6 | OUG | Oughtragh | 0.989 | 10.6 | 10.6 | 10.6 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
OUG | Oughtragh | 0.998 | 27.6 | 28.2 | 28 | 28.1 | 28.1 | 28.2 | 28.4 | 28.6 | 28.9 | 29.1 | PB | Poolbeg | 0.989 | 143.8 | 146.4 | 145.2 | 143.3 | 142.8 | 142.7 | 143.1 | 144 | 145.1 | 145.7 | PB | Poolbeg | 0.995 | 73.7 | 73.6 | 73.5 | 73.3 | 73.2 | 73.1 | 73 | 72.9 | 72.9 | 72.8
PB | Poolbeg | 0.989 | 186.2 | 190.2 | 189.1 | 189.7 | 190 | 190.6 | 191.7 | 193.2 | 195.5 | 196.7 | PLA | Platin | 0.95 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | PLA | Platin | 0.95 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
PLA | Platin | 0.95 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | PLS | Portlaoise 110kV | 0.979 | 43.2 | 44 | 43.6 | 43 | 42.9 | 42.9 | 43 | 43.3 | 43.6 | 43.8 | PLS | Portlaoise 110kv | 0.996 | 17.7 | 17.6 | 17.6 | 17.6 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.4
PLS | Portlaoise | 0.984 | 55.9 | 57.1 | 56.8 | 57 | 57.1 | 57.2 | 57.6 | 58 | 58.7 | 59.1 | RAT | Rathkeale | 0.993 | 33.4 | 34 | 33.7 | 33.3 | 33.2 | 33.2 | 33.3 | 33.5 | 33.7 | 33.9 | RAT | Rathkeale | 0.997 | 9.8 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.6 | 9.6 | 9.6
RAT | Rathkeale | 0.996 | 43.3 | 44.2 | 43.9 | 44.1 | 44.1 | 44.3 | 44.6 | 44.9 | 45.4 | 45.7 | RAT (N) | Rathgael | 0.99 | 16.9 | 17.3 | 17.1 | 17.5 | 17.6 | 17.7 | 17.7 | 17.8 | 17.9 | 18 | RAT (N) | Rathgael | 0.99 | 16.9 | 17.3 | 17.1 | 17.5 | 17.6 | 17.7 | 17.7 | 17.8 | 17.9 | 18
RAT (N) | Rathgael | 0.99 | 57.9 | 58.9 | 58.4 | 59.6 | 60 | 60.3 | 60.6 | 60.9 | 61.2 | 61.6 | RIC | Richmond | 0.972 | 29.1 | 29.6 | 29.4 | 29 | 28.9 | 28.9 | 29 | 29.2 | 29.4 | 29.5 | RIC | Richmond | 0.997 | 11.9 | 11.9 | 11.9 | 11.9 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8
RIC | Richmond | 0.98 | 37.7 | 38.5 | 38.3 | 38.4 | 38.5 | 38.6 | 38.8 | 39.1 | 39.6 | 39.8 | RNW | Rinawade | 0.95 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | RNW | Rinawade | 0.95 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1
RNW | Rinawade | 0.95 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | ROS | Rosebank | 0.99 | 8.9 | 8.2 | 8.1 | 8.3 | 8.3 | 8.4 | 8.4 | 8.4 | 8.5 | 8.5 | ROS | Rosebank | 0.99 | 8.9 | 8.2 | 8.1 | 8.3 | 8.3 | 8.4 | 8.4 | 8.4 | 8.5 | 8.5
ROS | Rosebank | 0.99 | 30.4 | 27.8 | 27.6 | 28.2 | 28.4 | 28.5 | 28.7 | 28.8 | 29 | 29.1 | RYB | Ryebrook | 0.95 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | RYB | Ryebrook | 0.95 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5
RYB | Ryebrook | 0.95 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | 104.5 | SBH | Snughborough | 0.95 | 14.3 | 14.3 | 17.1 | 19 | 21.9 | 23.8 | 14.3 | 28.5 | 31.4 | 33.3 | SBH | Snughborough | 0.95 | 14.3 | 14.3 | 17.1 | 19 | 21.9 | 23.8 | 14.3 | 28.5 | 31.4 | 33.3
SBH | Snughborough | 0.95 | 14.3 | 14.3 | 17.1 | 19 | 21.9 | 23.8 | 14.3 | 28.5 | 31.4 | 33.3 | SCR | Screebe | 0.999 | 13.4 | 13.6 | 13.5 | 13.3 | 13.3 | 13.3 | 13.3 | 13.4 | 13.5 | 13.6 | SCR | Screebe | 0.976 | 7.7 | 7.7 | 7.7 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6
SCR | Screebe | 0.992 | 17.3 | 17.7 | 17.6 | 17.7 | 17.7 | 17.7 | 17.9 | 18 | 18.2 | 18.3 | SHE | Shelton Abbey | 0.95 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | SHE | Shelton Abbey | 0.95 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
SHE | Shelton Abbey | 0.95 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | SHL | Salthill | 0.997 | 35 | 35.7 | 35.4 | 34.9 | 34.8 | 34.8 | 34.9 | 35.1 | 35.4 | 35.5 | SHL | Salthill | 0.997 | 14.1 | 14 | 14 | 14 | 14 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
SHL | Salthill | 1 | 45.4 | 46.4 | 46.1 | 46.2 | 46.3 | 46.4 | 46.7 | 47.1 | 47.7 | 47.9 | SKL | Shankill | 0.993 | 45.8 | 46.6 | 46.3 | 45.7 | 45.5 | 45.5 | 45.6 | 45.9 | 46.2 | 46.4 | SKL | Shankill | 0.997 | 11.6 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.4 | 11.4 | 11.4
SKL | Shankill | 0.995 | 59.3 | 60.6 | 60.2 | 60.4 | 60.5 | 60.7 | 61.1 | 61.6 | 62.3 | 62.7 | SLI | Sligo | 0.996 | 43.8 | 44.6 | 44.2 | 43.7 | 43.5 | 43.5 | 43.6 | 43.9 | 44.2 | 44.4 | SLI | Sligo | 1 | 16.6 | 16.6 | 16.5 | 16.5 | 16.5 | 16.5 | 16.4 | 16.4 | 16.4 | 16.4
SLI | Sligo | 0.997 | 56.7 | 58 | 57.6 | 57.8 | 57.9 | 58.1 | 58.4 | 58.9 | 59.6 | 59.9 | SNG | Singland | 0.992 | 14.1 | 14.3 | 14.2 | 14 | 14 | 14 | 14 | 14.1 | 14.2 | 14.3 | SNG | Singland | 1 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.4 | 5.4
SNG | Singland | 0.995 | 18.2 | 18.6 | 18.5 | 18.6 | 18.6 | 18.6 | 18.8 | 18.9 | 19.1 | 19.2 | SOM | Somerset | 0.974 | 18.3 | 18.7 | 18.5 | 18.3 | 18.2 | 18.2 | 18.2 | 18.4 | 18.5 | 18.6 | SOM | Somerset | 0.998 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1
SOM | Somerset | 0.989 | 23.7 | 24.2 | 24.1 | 24.2 | 24.2 | 24.3 | 24.4 | 24.6 | 24.9 | 25.1 | SPR | Springtown | 0.98 | 13.9 | 14.2 | 14 | 14.3 | 14.4 | 14.5 | 14.6 | 14.6 | 14.7 | 14.8 | SPR | Springtown | 0.98 | 13.9 | 14.2 | 14 | 14.3 | 14.4 | 14.5 | 14.6 | 14.6 | 14.7 | 14.8
SPR | Springtown | 0.98 | 47.6 | 48.4 | 48 | 49 | 49.3 | 49.5 | 49.7 | 50 | 50.3 | 50.6 | STR | Stratford | 0.958 | 18.7 | 19 | 18.9 | 18.6 | 18.6 | 18.5 | 18.6 | 18.7 | 18.9 | 18.9 | STR | Stratford | 1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5
STR | Stratford | 0.989 | 24.2 | 24.7 | 24.6 | 24.7 | 24.7 | 24.8 | 24.9 | 25.1 | 25.4 | 25.6 | STR (N) | Strabane | 0.99 | 12.4 | 12.6 | 12.5 | 12.8 | 12.8 | 12.9 | 13 | 13 | 13.1 | 13.2 | STR (N) | Strabane | 0.99 | 12.4 | 12.6 | 12.5 | 12.8 | 12.8 | 12.9 | 13 | 13 | 13.1 | 13.2
STR (N) | Strabane | 0.99 | 42.3 | 43.1 | 42.7 | 43.6 | 43.8 | 44.1 | 44.3 | 44.5 | 44.8 | 45 | TBG | Trabeg | 0.994 | 57 | 58 | 57.5 | 56.8 | 56.6 | 56.6 | 56.7 | 57.1 | 57.5 | 57.8 | TBG | Trabeg | 1 | 27 | 26.9 | 26.9 | 26.8 | 26.8 | 26.8 | 26.7 | 26.7 | 26.7 | 26.6
TBG | Trabeg | 0.997 | 73.8 | 75.4 | 74.9 | 75.2 | 75.3 | 75.5 | 76 | 76.6 | 77.5 | 78 | TBK | Tullabrack | 0.931 | 10 | 10.2 | 10.1 | 9.9 | 9.9 | 9.9 | 9.9 | 10 | 10.1 | 10.1 | TBK | Tullabrack | 0.992 | 1.9 | 1.9 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
TBK | Tullabrack | 0.961 | 12.9 | 13.2 | 13.1 | 13.2 | 13.2 | 13.2 | 13.3 | 13.4 | 13.6 | 13.7 | THU | Thurles | 0.983 | 23.4 | 23.8 | 23.7 | 23.3 | 23.3 | 23.3 | 23.3 | 23.5 | 23.6 | 23.7 | THU | Thurles | 0.99 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.5 | 10.5 | 10.5 | 10.5
THU | Thurles | 0.982 | 30.3 | 31 | 30.8 | 30.9 | 30.9 | 31 | 31.2 | 31.5 | 31.9 | 32 | TIP | Tipperary | 0.986 | 16.6 | 16.9 | 16.8 | 16.5 | 16.5 | 16.5 | 16.5 | 16.6 | 16.8 | 16.8 | TIP | Tipperary | 0.992 | 7.3 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2
TIP | Tipperary | 0.984 | 21.5 | 22 | 21.8 | 21.9 | 21.9 | 22 | 22.1 | 22.3 | 22.6 | 22.7 | TLK | Trillick | 0.968 | 17.6 | 18 | 17.8 | 17.6 | 17.5 | 17.5 | 17.6 | 17.7 | 17.8 | 17.9 | TLK | Trillick | 0.994 | 5.9 | 5.9 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8
TLK | Trillick | 0.987 | 22.9 | 23.3 | 23.2 | 23.3 | 23.3 | 23.4 | 23.5 | 23.7 | 24 | 24.1 | TON | Tonroe | 0.925 | 11.8 | 12.1 | 12 | 11.8 | 11.8 | 11.8 | 11.8 | 11.9 | 12 | 12 | TON | Tonroe | 0.987 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1
TON | Tonroe | 0.988 | 15.3 | 15.7 | 15.6 | 15.6 | 15.7 | 15.7 | 15.8 | 15.9 | 16.1 | 16.2 | TRI | Trien | 1 | 14.1 | 14.4 | 14.2 | 14.1 | 14 | 14 | 14 | 14.1 | 14.2 | 14.3 | TRI | Trien | 0.962 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1
TRI | Trien | 0.992 | 18.3 | 18.7 | 18.5 | 18.6 | 18.6 | 18.7 | 18.8 | 19 | 19.2 | 19.3 | TRL | Tralee | 0.99 | 45 | 45.8 | 45.4 | 44.8 | 44.7 | 44.7 | 44.8 | 45.1 | 45.4 | 45.6 | TRL | Tralee | 0.997 | 15.1 | 15.1 | 15.1 | 15 | 15 | 15 | 15 | 15 | 15 | 14.9
TRL | Tralee | 0.992 | 58.3 | 59.5 | 59.2 | 59.4 | 59.4 | 59.6 | 60 | 60.5 | 61.2 | 61.5 | TSB | Thornsberry | 0.977 | 27.9 | 28.4 | 28.1 | 27.8 | 27.7 | 27.7 | 27.7 | 27.9 | 28.1 | 28.2 | TSB | Thornsberry | 0.996 | 11 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.8 | 10.8 | 10.8
TSB | Thornsberry | 0.986 | 36.1 | 36.9 | 36.6 | 36.8 | 36.8 | 36.9 | 37.2 | 37.4 | 37.9 | 38.1 | WAR | Waringstown | 0.99 | 19.4 | 19.8 | 19.6 | 20 | 20.1 | 20.2 | 20.3 | 20.4 | 20.5 | 20.6 | WAR | Waringstown | 0.99 | 19.4 | 19.8 | 19.6 | 20 | 20.1 | 20.2 | 20.3 | 20.4 | 20.5 | 20.6
WAR | Waringstown | 0.99 | 66.2 | 67.4 | 66.8 | 68.2 | 68.6 | 69 | 69.2 | 69.6 | 70 | 70.4 | WAT | Waterford | 0.986 | 43.3 | 44.1 | 43.7 | 43.1 | 43 | 43 | 43.1 | 43.4 | 43.7 | 43.9 | WAT | Waterford | 1 | 29 | 28.9 | 28.9 | 28.8 | 28.8 | 28.7 | 28.7 | 28.7 | 28.6 | 28.6
WAT | Waterford | 0.996 | 56.1 | 57.3 | 56.9 | 57.1 | 57.2 | 57.4 | 57.7 | 58.2 | 58.9 | 59.2 | WEX | Wexford | 0.979 | 47.1 | 48 | 47.6 | 47 | 46.8 | 46.8 | 46.9 | 47.2 | 47.6 | 47.8 | WEX | Wexford | 1 | 20.9 | 20.8 | 20.8 | 20.8 | 20.7 | 20.7 | 20.7 | 20.7 | 20.6 | 20.6
WEX | Wexford | 0.985 | 61.1 | 62.4 | 62 | 62.2 | 62.3 | 62.5 | 62.8 | 63.4 | 64.1 | 64.5 | WHI | Whitegate | 0.95 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | WHI | Whitegate | 0.95 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
WHI | Whitegate | 0.95 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9

## generation
Table D-1 MEC of Existing and Committed Transmission-Connected Generation | [7 empty] | Table D-2 Existing and Committed Distribution-Connected Wind Farm Capacity | [11 empty] | Table D-3 Existing and Committed Distribution-Connected Generation (excluding wind)
[6 empty] | Connection Year (if future) | Maximum Export Capacity (MW) | Area | 110 kV Station | Maximum Export Capacity (MEC) | [9 empty] | Area | 110 kV Station | Type | Maximum Export Capacity (MEC)
Area | Generation Station | Unit ID | Connected At |  | Fuel Type |  |  |  |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  |  |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| Carrickaduff |  | Croaghnagawna | 110 kV | Wind | 2023 | 66 |  | Ardnagappary | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 |  | Binbane | Hydro | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
| Carrickalangan |  | Croaghnagawna | 110 kV | Wind | 2023 | 72 |  | Binbane | 49.3 | 60.6 | 60.6 | 60.6 | 66.6 | 66.6 | 66.6 | 66.6 | 66.6 | 66.6 |  | Crane | Battery |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Erne Cathleens Fall Hydro (3) |  | Cathaleen’s Fall | 110 kV | Hydro |  | 22 |  | Cath_Fall | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 |  | Crane | PV |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5
| Erne Cathleens Fall Hydro (4) | ER3 | Cathaleen’s Fall | 110 kV | Hydro |  | 23 |  | Corderry | 63.3 | 63.3 | 63.3 | 63.3 | 63.3 | 63.3 | 63.3 | 63.3 | 63.3 | 63.3 |  | Crane | PV |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Erne Cliff Hydro (1) | ER4 | Cliff | 110 kV | Hydro |  | 10 |  | Crane | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 |  | Crane | Solar |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
| Erne Cliff Hydro (2) | ER1 | Cliff | 110 kV | Hydro |  | 10 |  | Drybridge | 7 | 7 | 7 | 7 | 11 | 11 | 11 | 11 | 11 | 11 |  | Drybridge | Biomass | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
| Firlough WF |  | Firlough | 110 kV | Wind |  | 48.3 |  | Dundalk | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 |  | Drybridge | LFG | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2
| Garvagh - Glebe (1a) | ER2 | Garvagh | 110 kV | Wind |  | 26 |  | Garvagh | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | Border | Drybridge | Solar |  | 4 | 4 | 4 | 16 | 16 | 16 | 16 | 16 | 16
| Garvagh - Tullynahaw (1c) |  | Garvagh | 110 kV | Wind |  | 22 |  | Glenree | 64.8 | 64.8 | 77.3 | 77.3 | 77.3 | 77.3 | 77.3 | 77.3 | 77.3 | 77.3 |  | Dundalk | Solar | [5 empty] | 4 | 4 | 4 | 4 | 4
| Golagh (1) |  | Golagh | 110 kV | Wind |  | 15 | Border | Gortawee | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Meath Hill | Battery |  |  |  | 33 | 33 | 33 | 33 | 33 | 33 | 33
| Lenalea |  | Lenalea | 110 kV | Wind | 2025 | 30.5 |  | Letterkenny | 51.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 |  | Meath Hill | CHP | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Border | Kingsmountain (1) |  | Cunghill | 110 kV | Wind |  | 24 |  | Lisdrum |  |  | 33.1 | 33.1 | 33.1 | 33.1 | 33.1 | 33.1 | 33.1 | 33.1 |  | Shankill | LFG | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
| Kingsmountain (2) |  | Cunghill | 110 kV | Wind |  | 11 |  | Meath Hill | 45.6 | 68.7 | 68.7 | 68.7 | 68.7 | 68.7 | 68.7 | 68.7 | 68.7 | 68.7 |  | Shankill | Solar |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Lisdrumdoagh Energy Storage Facility |  | Lisdrum | 110 kV | Battery |  | 60 |  | Moy | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | Somerset | Solar |  |  |  |  | 4 | 4 | 4 | 4 | 4 | 4
| Meentycat (1) |  | Meentycat | 110 kV | Wind |  | 71 |  | Shankill | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | Stevenstown | Battery |  |  |  |  | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
| Meentycat (2) |  | Meentycat | 110 kV | Wind |  | 14 |  | Sligo | 13.7 | 13.7 | 13.7 | 13.7 | 13.7 | 13.7 | 13.7 | 13.7 | 13.7 | 13.7 |  | Stevenstown | Solar | [5 empty] | 4.95 | 4.95 | 4.95 | 4.95 | 4.95
| Mountain Lodge (1) |  | Ratrussan | 110 kV | Wind |  | 31 |  | Somerset | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 |  | Trien | Solar
| Mullygaffy |  | Tievebrack | 110 kV | Wind |  | 29.9 |  | Sorne Hill | 63.3 | 63.3 | 63.3 | 63.3 | 63.3 | 63.3 | 63.3 | 63.3 | 63.3 | 63.3 |  | Blackrock | CHP | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
| Mulreavy (1) |  | Mulreavy | 110 kV | wind |  | 82 |  | Trien | 72.7 | 72.7 | 72.7 | 72.7 | 72.7 | 72.7 | 72.7 | 72.7 | 72.7 | 72.7 |  | Blackrock | CHP | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
| Mulreavy Ext |  | Mulreavy | 110 kV | Wind |  | 13 |  | Trillick | 44.7 | 44.7 | 44.7 | 44.7 | 44.7 | 44.7 | 44.7 | 44.7 | 44.7 | 44.7 |  | Fin_rural | CHP | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Oriel (1) |  | Oriel | 0.69 kV | Wind | 2022 | 210 |  | Glasmore | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  | Finglas | Solar |  |  |  |  | 8.42 | 8.42 | 8.42 | 8.42 | 8.42 | 8.42
| Ratrussan (1a) |  | Ratrussan | 110 kV | Wind |  | 48 | Dublin | Nangor | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | Dublin | Glasmore | CHP | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7
| Corduff |  | Corduff | 220 kV | Battery | 2022 | 70 |  | Poppintree | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Glasmore | Solar |  |  |  |  | 4 | 4 | 4 | 4 | 4 | 4
| Dublin Bay Power |  | Irishtown | 220 kV | Gas/Oil |  | 422 | Mid- East | Arklow | 79.7 | 85.7 | 85.7 | 85.7 | 85.7 | 85.7 | 85.7 | 85.7 | 85.7 | 85.7 |  | Ringsend | Diesel | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
| Gallanstown Solar |  | Gallanstown | 110 kV | Solar | 2023 | 119 | Mid- lands | Blake | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Ringsend | Waste to Energy | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
| Harristown Solar PV |  | Harristown | 110 kV | Solar | 2023 | 42 |  | Dallow | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | Baltrasna | Solar |  |  |  |  | 10 | 10 | 10 | 10 | 10 | 10
| Huntstown (1) | HNC | Huntstown | 220 kV | Gas/Oil |  | 236 |  | Lanesboro | 4.6 | 4.6 | 4.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 |  | Baltrasna | Solar | [5 empty] | 10 | 10 | 10 | 10 | 10
Dublin | Huntstown (1) | HNC | Huntstown | 220 kV | Gas/Oil |  | 123 |  | Ardnacrusha | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 |  | Arklow | Biomass | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Huntstown (2) | HN2 | Huntstown | 220 kV | Gas |  | 412 |  | Booltiagh | 85.4 | 85.4 | 85.4 | 93.4 | 108.4 | 108.4 | 108.4 | 108.4 | 108.4 | 108.4 |  | Arklow | Solar | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Shellybanks Com- bined Cycle | PBC | Shellybanks | 220 kV | Gas/Oil |  | 150 |  | Bunkimalt | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 |  | Arklow | Solar |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Shellybanks Com- bined Cycle | PBC | Shellybanks | 220 kV | Gas/Oil |  | 150 |  | Cauteen | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 |  | Dunfirth | Solar |  | 4 | 4 | 4 | 8 | 8 | 8 | 8 | 8 | 8
| Shellybanks Com- bined Cycle | PBC | Shellybanks | 220 kV | Gas/Oil |  | 173 |  | Charleville | 70.7 | 70.7 | 70.7 | 70.7 | 70.7 | 70.7 | 70.7 | 70.7 | 70.7 | 70.7 | Mid-East | Griffinrath | Hydro | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Blundlestown |  | Blundelstown | 110 kV | Solar |  | 60 | Mid- West | Cureeny T | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | Griffinrath | Solar |  |  |  |  | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
| Cloncreen Wind farm |  | Cloncreen | 110 kV | Wind | 2025 | 75 |  | Ikerrin | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | Kilteel | LFG + | 9.77 | 9.77 | 9.77 | 9.77 | 9.77 | 9.77 | 9.77 | 9.77 | 9.77 | 9.77
| Gaskinstown |  | Deenes | 110 kV | Solar | 2022 | 85 |  | Lisheen | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 |  |  | Diesel
| Gillinstown Solar |  | Garballagh | 110 kV | Solar | 2023 | 95 |  | Nenagh | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | Kilteel | Solar |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
| Gorman BES |  | Gorman | 110 kV | Battery | 2023 | 50 |  | Rathkeale | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 |  | Monread | Solar | 4 | 4 | 4 | 4 | 8 | 8 | 8 | 8 | 8 | 8
| Liffey Hydro (1) | LI1 | Pollaphuca | 110 kV | Hydro |  | 15 |  | Thurles | 41.8 | 41.8 | 41.8 | 41.8 | 41.8 | 41.8 | 41.8 | 41.8 | 41.8 | 41.8 |  | Newbridge | Solar |  | 3.99 | 3.99 | 3.99 | 15.99 | 15.99 | 15.99 | 15.99 | 15.99 | 15.99
| Liffey Hydro (2) | LI2 | Pollaphuca | 110 kV | Hydro |  | 15 |  | Tipperary | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Athlone | LFG | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Mid-East | Liffey Hydro (4) | LI4 | Pollaphuca | 110 kV | Hydro |  | 4 |  | Tullabrack | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | Athlone | Solar | [5 empty] | 8 | 8 | 8 | 8 | 8
| Porterstown BES |  | Kilteel | 110 kV | Battery |  | 30 |  | Aghyoule | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 |  | Blake | Solar |  |  |  |  | 5 | 5 | 5 | 5 | 5 | 5
| Timahoe North |  | Timahoe | 110 kV | Solar | 2023 | 70 |  | Garvagh | 47.5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Blake | LFG | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
| Turlough Hill (1) | TH1 | Turlough Hill | 220 kV | Pumped Storage |  | 73 |  | Antrim | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 |  | Derryiron | Flywheel |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
| Turlough Hill (2) | TH2 | Turlough Hill | 220 kV | Pumped Storage |  | 73 |  | Ballymena | 53.8 | 53.8 | 53.8 | 53.8 | 53.8 | 53.8 | 53.8 | 53.8 | 53.8 | 53.8 | Midland | Lanesboro | Solar |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Turlough Hill (3) | TH3 | Turlough Hill | 220 kV | Pumped Storage |  | 73 |  | Brockaghboy | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 |  | Mullingar | Solar | 4 | 8 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12
| Turlough Hill (4) | TH4 | Turlough Hill | 220 kV | Pumped Storage |  | 73 |  | Carnmoney | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 |  | Navan | CHP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
| Blackwater Bog Solar 1 |  | Derrylahan | 110 kV | solar | 2023 | 65 |  | Coleraine | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | Navan | Solar | 4 | 9 | 9 | 13 | 17 | 17 | 17 | 17 | 17 | 17
| Clonfad Solar |  | Clonfad | 110 kV | solar | 2022 | 100 |  | Coolkeeragh | 12 | 12 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 |  | Richmond | Solar |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Cloghan Wind Farm |  | Derrycarney | 110 kV | Wind | 2024 | 34 |  | Creagh | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Thornsberry | CHP |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Edenderry Peaking | ED3 | Cushaling | 110 kV | Conventional |  | 117 |  | Drumquin | 67.9 | 67.9 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 |  | Thornsberry | Solar |  |  |  |  | 4 | 8 | 8 | 8 | 8 | 8
Midlands | Edenderry Power | ED1 | Cushaling | 110 kV | Peat |  | 134 |  | Drumnakelly | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 |  | Ballydine | Biogas | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44
| Lanesboro (2) |  | Lanesboro | 110 kV | Peat |  | 40 | North- ern Ireland | Dungannon | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 |  | Ballydine | Solar |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Lanesboro (3) |  | Lanesboro | 110 kV | Peat |  | 45 |  | Eden | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 |  | Cahir | Solar | 8 | 12 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31
| Loughteague |  | Coolnabacky | 110 kV | solar | 2025 | 55 |  | Enniskillen | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | Mid-West | Drumline | Solar |  |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| Lumcloon Batt |  | Derrycarney | 110 kV | Battery |  | 100 |  | Kells |  |  | 68.1 | 68.1 | 68.1 | 68.1 | 68.1 | 68.1 | 68.1 | 68.1 |  | Rathkeale | Biogas | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44
| Mountlucas (1) |  | Mountlucas | 110 kV | Wind |  | 79 |  | Killymallaght | 35.7 | 35.7 | 35.7 | 35.7 | 35.7 | 35.7 | 35.7 | 35.7 | 35.7 | 35.7 |  | Rathkeale | CHP | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
| Rhode PCP (1) | RP1 | Derryiron | 110 kV | Distillate |  | 52 |  | Larne | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | Rathkeale | LFG | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
| Rhode PCP (2) | RP2 | Derryiron | 110 kV | Distillate |  | 52 |  | Limavady | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 |  | Antrim | PV | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8
| Alumina CHP (1) | SK3 | Aughinish | 110 kV | Gas |  | 86 |  | Lisaghmore | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | Ballymena | PV | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Alumina CHP (1) | SK4 | Aughinish | 110 kV | Gas |  | 86 |  | Loguestown | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 |  | Coolkeeragh | Bio | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6
| Ardnacrusha Hydro (1) | AA1 | Ardnacrusha | 110 kV | Hydro |  | 21 |  | Magherakeel | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | Northern Ireland | Lisburn | PV | 58.85 | 58.85 | 58.85 | 58.85 | 58.85 | 58.85 | 58.85 | 58.85 | 58.85 | 58.85
| Ardnacrusha Hydro (2) | AA2 | Ardnacrusha | 110 kV | Hydro |  | 22 |  | Omagh | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 |  | Newtownards | PV | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99
| Ardnacrusha Hydro (3) | AA3 | Ardnacrusha | 110 kV | Hydro |  | 19 |  | Rasharkin | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 |  | Rasharkin | PV | 35.01 | 35.01 | 35.01 | 35.01 | 35.01 | 35.01 | 35.01 | 35.01 | 35.01 | 35.01
| Ardnacrusha Hydro (4) | AA4 | Ardnacrusha | 110 kV | Hydro |  | 24 |  | Slieve Kirk | 73.6 | 73.6 | 73.6 | 73.6 | 73.6 | 73.6 | 73.6 | 73.6 | 73.6 | 73.6 |  | Rosebank | BIO | 9.98 | 9.98 | 9.98 | 9.98 | 9.98 | 9.98 | 9.98 | 9.98 | 9.98 | 9.98
| Boolinrudda |  | Ennis | 110 kV | Wind |  | 46 |  | Strabane | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 |  | Waringstown | PV | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Booltiagh (1) |  | Booltiagh | 110 kV | Wind |  | 19 |  | Tremoge | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 |  | Athy | Solar | 4 | 4 | 4 | 4 | 4 | 8.99 | 8.99 | 8.99 | 8.99 | 8.99
Mid-West | Booltiagh (2) |  | Booltiagh | 110 kV | Wind |  | 12 |  | Barrymore | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 |  | Athy | Battery |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
| Dromada (1) |  | Dromada | 110 kV | Wind |  | 29 |  | Butlerstown | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 |  | Ballybeg | LFG | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
| Kill Hill (1) |  | Kill Hill | 110 kV | Wind |  | 36 |  | Carlow | 34.4 | 34.4 | 34.4 | 34.4 | 34.4 | 34.4 | 34.4 | 34.4 | 34.4 | 34.4 |  | Ballybeg | Solar |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
| Knockalassa |  | Ennis | 110 kV | Wind |  | 27 | South- East | Dungarvan | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 |  | Banoge | Battery |  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Lisheen (1) |  | Lisheen | 110 kV | Wind |  | 36 |  | Lodgewood | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 |  | Banoge | Solar |  | 4 | 4 | 4 | 8 | 8 | 8 | 8 | 8 | 8
| Lisheen (1a) |  | Lisheen | 110 kV | Wind |  | 19 |  | Portlaoise | 54.2 | 54.2 | 54.2 | 54.2 | 54.2 | 54.2 | 54.2 | 54.2 | 54.2 | 54.2 |  | Barrymore | CHP | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
| Lisheen 3 |  | Lisheen | 110 kV | Wind | 2022 | 29 |  | Waterford | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | Barrymore | Solar |  |  |  | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
| Moneypoint (1) | MP1 | MNYPG3 | 380 kV | Coal |  | 302 |  | Wexford | 38.9 | 38.9 | 38.9 | 38.9 | 38.9 | 38.9 | 38.9 | 38.9 | 38.9 | 38.9 |  | Butlerstown | Solar | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Moneypoint (2) | MP2 | MNYPG3 | 380 kV | Coal |  | 305 |  | Athea | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 |  | Coolroe | Solar |  |  |  |  | 10 | 10 | 10 | 10 | 10 | 10
| Moneypoint (3) | MP3 | MNYPG3 | 380 kV | Coal |  | 302 |  | Ballylickey | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | South-East | Cow Cross | Solar |  |  |  |  | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95
| Moneypoint WF |  | MNYPG3 | 380 kV | Wind |  | 18 |  | Bandon | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 |  | Doon | Hydro | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Ballylumford | BGT20 | Ballylumford | 275 kV | Gas |  | 500 |  | Boggeragh | 20 | 26 | 26 | 38 | 41 | 41 | 41 | 41 | 41 | 41 |  | Doon | Solar |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8
| Ballylumford 10 | B10 | Ballylumford Power Station | 110 kV | Gas |  | 100 |  | Castleview | - | - | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Dungarvan | Solar |  |  |  |  | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99
| Ballylumford GT1 |  | Ballylumford Power Station | 110 kV | Gas |  | 58 |  | Cloghboola | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 |  | Great Island | Battery |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30
| Ballylumford GT2 |  | Ballylumford Power Station | 110 kV | Gas |  | 58 |  | Coomataggart | 42.6 | 42.6 | 42.6 | 42.6 | 42.6 | 42.6 | 42.6 | 42.6 | 42.6 | 42.6 |  | Great Island | Solar |  | 5 | 5 | 5 | 17 | 17 | 17 | 17 | 17 | 17
| Castlereagh BES |  | Castlereagh | 110 kV | Battery | 2023 | 50 |  | Cordal | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 |  | Kilkenny | Solar | 4 | 4 | 4 | 4 | 8 | 8 | 8 | 8 | 8 | 8
| Coolkeeragh GT | C30 GT | Coolkeeragh Power Station | 275 kV | Gas |  | 260 | South- West | Dunmanway | 42.3 | 42.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 |  | Kilkenny | CHP | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| Coolkeeragh GT8 | CGT8 | Coolkeeragh Power Station | 110 kV | Oil |  | 53 |  | Garrow | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | Portlaoise | Biogas | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Northern Ireland | Coolkeeragh ST | C30 GS | Coolkeeragh Power Station | 110 kV | Gas |  | 170 |  | Glenlara | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | Portlaoise | Solar |  |  |  | 4 | 8 | 8 | 8 | 8 | 8 | 8
| Kilroot GT3 | KGT3 | Kilroot Power Station | 275 kV | Distillate |  | 42 |  | Kilbarry | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  | Waterford | Solar |  | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99
| Kilroot GT4 | KGT4 | Kilroot Power Station | 275 kV | Distillate |  | 42 |  | Kilpaddoge | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | Wexford | CHP | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
| KELLS_BES |  | Kells | 110 kV | Battery | 2023 | 50 |  | Knockeragh | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 |  | Wexford | Solar |  | 3.99 | 3.99 | 19.99 | 19.99 | 19.99 | 19.99 | 19.99 | 19.99 | 19.99
| Kilroot OCGT6 |  | Kilroot Power Station | 275 kV | Gas | 2023 | 406 |  | Macroom | 34.1 | 34.1 | 34.1 | 34.1 | 34.1 | 34.1 | 34.1 | 34.1 | 34.1 | 34.1 |  | Ahane | Solar | [5 empty] | 4 | 4 | 4 | 4 | 4
| Kilroot OCGT7 |  | Kilroot Power Station | 275 kV | Gas | 2023 | 302 |  | Midleton | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 |  | Bandon | Solar |  |  | 9.94 | 9.94 | 19.84 | 19.84 | 19.84 | 19.84 | 19.84 | 19.84
| Kilroot ST1 | K1 | Kilroot Power Station | 275 kV | Coal/Oil |  | 195 |  | Oughtragh | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | Barnahely | Solar | [5 empty] | 5 | 5 | 5 | 5 | 5
| Kilroot ST2 | K2 | Kilroot Power Station | 275 kV | Coal/Oil |  | 195 |  | Reamore | 57.9 | 57.9 | 83.2 | 83.2 | 83.2 | 83.2 | 83.2 | 83.2 | 83.2 | 83.2 |  | Castleview | Biogas |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Tamnamore BES |  | TAMNAMORE | 110 kV | Battery |  | 50 |  | Tralee | 45.9 | 45.9 | 45.9 | 45.9 | 45.9 | 45.9 | 45.9 | 45.9 | 45.9 | 45.9 |  | Castleview | CHP | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Tandragee BES |  | Tandragee | 110 kV | Battery |  | 50 |  | Arigna | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 |  | Dunmanway | Biogas | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Ballywater |  | Ballywater | 110 kV | Wind |  | 42 |  | Bellacorick | 9 | 9 | 75.8 | 75.8 | 78.3 | 78.3 | 78.3 | 78.3 | 78.3 | 78.3 |  | Glenlara | Solar |  |  |  |  | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95
| Castledockrell |  | Castledockrill | 110 kV | Wind |  | 42 |  | Castlebar | 43.6 | 43.6 | 43.6 | 43.6 | 43.6 | 43.6 | 43.6 | 43.6 | 43.6 | 43.6 |  | Kilbarry | Solar |  | 4.95 | 4.95 | 4.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
| Great Island CCGT | GI4 | Great Island | 220 kV | Conven- tional |  | 439 |  | Cloon | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | South-West | Knockeragh | Biomass | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
South-East | Knocknamona |  | Dungarvan | 110 kV | Wind |  | 34 | West | Dalton | 43.4 | 43.4 | 43.4 | 43.4 | 43.4 | 43.4 | 43.4 | 43.4 | 43.4 | 43.4 |  | Knockeragh | Solar |  |  |  | 8.99 | 8.99 | 8.99 | 8.99 | 8.99 | 8.99 | 8.99
| Rathnaskilloge |  | Rathnaskillo | 110 kV | solar | 2023 | 95 |  | Salthill | 46.1 | 46.1 | 46.1 | 46.1 | 46.1 | 46.1 | 46.1 | 46.1 | 46.1 | 46.1 |  | Limerick | Solar |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Rosspile Solar Farm |  | Rosspile | 110 kV | Solar | 2023 | 95 |  | Screeb | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Macroom | Solar |  |  |  |  | 4 | 4 | 4 | 4 | 4 | 4
| Woodhouse |  | Woodhouse | 110 kV | Wind |  | 20 |  | Tawnaghmore | 19.2 | 19.2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | Mallow | Solar | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95
| Aghada CCGT | AD2 | Aghada | 220 kV | Gas |  | 442 |  | Tonroe | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 |  | Midleton | Solar |  |  |  |  | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95
| Aghada | AT1 | Aghada | 220 kV | Gas |  | 90 | [13 empty] | Oughtragh | Solar |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Aghada | AT2 | Aghada | 220 kV | Gas |  | 90 | [13 empty] | Reamore | Battery | - | - | - | 8 | 8 | 8 | 8 | 8 | 8 | 8
| Aghada | AT4 | Aghada | 220 kV | Gas |  | 90 | [13 empty] | Trabeg | Solar |  |  | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95
| Aghada BESS 1 |  | Aghada | 220 kV | storage |  | 19 | [13 empty] | Tralee | Solar |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Aghada BESS 2 |  | Aghada | 220 kV | Storage |  | 159 | [13 empty] | Bellacorick | Wave | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Athea |  | Athea | 110 kV | Wind |  | 34 | [13 empty] | Carrick on Shannon
| Ballinknockane Solar Farm |  | Ballinknockane | 110 kV | Solar | 2023 | 50 | [14 empty] | Solar |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Banemore Solar Farm |  | Clahane | 110 kV | Solar |  | 34 | [12 empty] | West | Cloon | Solar |  | 4 | 4 | 4 | 24 | 24 | 24 | 24 | 24 | 24
| Boggeragh (1) |  | Boggeragh | 110 kV | Wind |  | 57 | [13 empty] | Dalton | Battery |  |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 12
| Boggeragh (2) |  | Boggeragh | 110 kV | Wind |  | 48 | [13 empty] | Dalton | Solar | [5 empty] | 4 | 4 | 4 | 4 | 4
| Clahane (1) |  | Clahane | 110 kV | Wind |  | 38 | [13 empty] | Tawnaghmore | Biomass |  |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
| Clahane (2) |  | Clahane | 110 kV | Wind |  | 14
| Cloghboola |  | Cloghboola | 110 kV | Wind |  | 46
| Coomacheo (1) |  | Garrow | 110 kV | Wind |  | 41
| Coomacheo (2) |  | Garrow | 110 kV | Wind |  | 18
South-West | Coomagearlahy (1) |  | Coomagearlahy | 110 kV | Wind |  | 43
| Coomagearlahy (2) |  | Coomagearlahy | 110 kV | Wind |  | 9
| Coomagearlahy (3) |  | Coomagearlahy | 110 kV | Wind |  | 30
| Cordal |  | Cordal | 110 kV | Wind |  | 90
| Drombeg Solar Park |  | Drombeg | 110 kV | Solar | 2022 | 50
| Glanlee (1) |  | Glanlee | 110 kV | Wind |  | 30
| Glen Solar |  | Glen | 110 kV | solar | 2024 | 40
| Grousemount |  | Coomataggart | 110 kV | Wind |  | 114
| Kelwin |  | Kilpaddoge | 220 kV | Wind |  | 27
| Kelwin Battery |  | Kilpaddoge | 220 kV | storage | 2024 | 42
| Killavoy |  | Boggeragh | 110 kV | Wind |  | 18
| Knockacummer (1) |  | Knockacummer | 110 kV | Wind |  | 105
| Lee Carrigadrohid Hydro (1) |  | Carrigadrohid | 110 kV | Hydro |  | 8
| Lee Inniscarra Hydro (1) |  | Inniscarra | 110 kV | Hydro |  | 19
| Tarbert (1) | TB1 | Tarbert | 110 kV | HFO |  | 57
| Tarbert (2) | TB2 | Tarbert | 110 kV | HFO |  | 57
| Tarbert (3) | TB3 | Tarbert | 220 kV | HFO |  | 256
| Tarbert (4) | TB4 | Tarbert | 220 kV | HFO |  | 258
| Tobertoreen |  | Athea | 110 kV | Wind |  | 34
| Tullabeg Solar Park |  | Tullabeg | 110 kV | Solar | 2023 | 50
| Whitegen CCGT | WG | Glanagow | 220 kV | Gas |  | 449
| Buffy |  | Buffy | 110 kV | Wind |  | 91
| Carrigdangan |  | Carrigdangan | 110 kV | Wind | 2023 | 68
| Derrybrien (1) |  | Derrybrien | 110 kV | Wind |  | 60
| Knockalough |  | Knockalough | 110 kV | Wind |  | 34
| Killala (1) |  | Tawnaghmore | 110 kV | Wind |  | 19
| Killala (2) |  | Tawnaghmore | 110 kV | Wind | 2023 | 11
| Oweninney (1) |  | Bellacorick | 110 kV | Wind |  | 89
| Oweninney (2) |  | Bellacorick | 110 kV | Wind |  | 83
| Oweninney (3) |  | Bellacorick | 110 kV | Wind | 2023 | 50
West | Seecon (1) |  | Knockranny | 110 kV | Wind |  | 108
| Shannonbridge ESS |  | Shannonbridge | 220 kV | Battery |  | 100
| Shannonbridge ESS |  | Shannonbridge | 220 kV | Wind |  | 63
| Shantallow Solar |  | Shantallow | 110 kV | Solar | 2023 | 35
| Sheskin |  | Bellacorick | 110 kV | Wind | 2023 | 33
| Sliabh Bawn (1) |  | Sliabh Bawn | 110 kV | Wind |  | 58
| Tawnaghmore Peak- ing Plant | TP1 | Tawnaghmore | 110 kV | distillate |  | 52
| Tawnaghmore Peak- ing Plant | TP2 | Tawnaghmore | 110 kV | distillate |  | 52
| Tynagh | TY1 | Tynagh | 220 kV | Gas |  | 268
| Tynagh | TY2 | Tynagh | 220 kV | Gas |  | 142
| Ugool |  | Uggool | 110 kV | Wind |  | 66

## gencost
Generator Technical Data - PUBLIC
Plant ID | [5 empty] | Fuel type |  |  |  |  | Capacity |  |  | Heat Rate Curve | [10 empty] | Forced Outages |  | TOD |  |  |  | Starts
Company Name | Jurisdiction | SEM Unit ID | Plexos Unit ID | Unit Name | Change Date for New Unit Characteristics | Start Fuel 1 | Percent 1 | Start Fuel 2 | Percent 2 | Fuel for Generation and No Load | Min Stable Capacity (MW) | Max Capacity (MW) | Summer Rating--Where Different (MW) | No Load Heat Requirement (GJ/hr) | Capacity point 1 (MW) | Capacity point 2 (MW) | Capacity point 3 (MW) | Capacity point 4 (MW) | Capacity point 5 (MW) | Heat Rate Inc 1 (GJ/MWh) | Heat Rate Inc 2 (GJ/MWh) | Heat Rate Inc 3 (GJ/MWh) | Heat Rate Inc 4 (GJ/MWh) | Heat Rate Inc 5 (GJ/MWh) | Forced Outage Rate,% | Mean Time to Repair, hrs | Ramp Rate Up, MW/min | Ramp Rate Down, MW/min | Min Up Time (hrs) | Min Down Time (hrs) | Start up Energy (GJ) Hot | Start up Energy (GJ) Warm | Start up Energy (GJ) Cold | Hot to Warm boundary, hrs | Warm to Cold boundary, hrs
ESB | ROI | GU_400200 | AA1 | Ardnacrusha 1 |  | Water | 100% |  |  | Water |  | 21 | [12 empty] | 4.5% | 86 | 0.42 | 0.42
ESB | ROI | GU_400201 | AA2 | Ardnacrusha 2 |  | Water | 100% |  |  | Water |  | 22 | [12 empty] | 4.5% | 86 | 0.47 | 0.47
ESB | ROI | GU_400202 | AA3 | Ardnacrusha 3 |  | Water | 100% |  |  | Water |  | 19 | [12 empty] | 4.5% | 86 | 0.33 | 0.33
ESB | ROI | GU_400203 | AA4 | Ardnacrusha 4 |  | Water | 100% |  |  | Water |  | 24 | [12 empty] | 4.5% | 82 | 0.55 | 0.55
ESB | ROI | GU_400850 | ADC | Aghada CCGT |  | Gas | 100% |  |  | Gas | 130 | 440 |  | 589.4 | 130 | 200 | 320 | 380 | 440 | 3.177 | 5.297 | 5.393 | 5.757 | 5.814 | 6.2% | 192 | 8.83 | 12.38 | 4 | 4 | 1200 | 1200 | 1200 | 12 | 60
ESB | ROI | GU_400181 | AT1 | Aghada CT 1 |  | Gas | 100% |  |  | Gas | 15 | 90 |  | 275.9 | 40 | 90 |  |  |  | 7.573 | 9.396 |  |  |  | 6.2% | 174 | 5 | 5 | 0.5 | 1 | 63 | 63 | 63 | 12 | 48
ESB | ROI | GU_400182 | AT2 | Aghada CT 2 |  | Gas | 100% |  |  | Gas | 15 | 90 |  | 275.9 | 40 | 90 |  |  |  | 7.573 | 9.396 |  |  |  | 6.2% | 174 | 5 | 5 | 0.5 | 1 | 63 | 63 | 63 | 12 | 48
ESB | ROI | GU_400183 | AT4 | Aghada CT 4 |  | Gas | 100% |  |  | Gas | 15 | 90 |  | 275.9 | 40 | 90 |  |  |  | 7.573 | 9.396 |  |  |  | 6.2% | 174 | 5 | 5 | 0.5 | 1 | 63 | 63 | 63 | 12 | 48
POWERNI | NI | GU_500140 | B10 | Ballylumford CCGT Unit 10 |  | Gas | 100% |  |  | Gas | 63 | 101 | 98.9 | 88.335 | 63 | 101 |  |  |  | 6.003 | 6.003 |  |  |  | 6.2% | 72 | 1.06 | 3.98 | 0.02 | 4 | 135 | 225 | 405 | 8 | 40
POWERNI | NI | GU_500130 | B31 | Ballylumford CCGT Unit 31 |  | Gas | 100% |  |  | Gas | 113 | 247 | 244.1 | 351 | 113 | 247 |  |  |  | 5.715 | 5.715 |  |  |  | 6.2% | 72 | 11 | 11 | 0.02 | 4 | 639 | 1134 | 2025 | 8 | 40
POWERNI | NI | GU_500131 | B32 | Ballylumford CCGT Unit 32 |  | Gas | 100% |  |  | Gas | 113 | 247 | 244.1 | 351 | 113 | 247 |  |  |  | 5.715 | 5.715 |  |  |  | 6.2% | 72 | 11 | 11 | 0.02 | 4 | 639 | 1134 | 2025 | 8 | 40
EP | NI | GU_500283 | BGT1 | Ballylumford GT1 |  | Gasoil | 100% |  |  | Gasoil | 8 | 58 |  | 180 | 8 | 53 | 58 |  |  | 11.05 | 11.05 | 11.05 |  |  | 2% | 24 | 10 | 18 | 0.02 | 0.25 | 8 | 8 | 8
EP | NI | GU_500284 | BGT2 | Ballylumford GT2 |  | Gasoil | 100% |  |  | Gasoil | 8 | 58 |  | 180 | 8 | 53 | 58 |  |  | 11.05 | 11.05 | 11.05 |  |  | 2% | 24 | 10 | 18 | 0.02 | 0.25 | 8 | 8 | 8
ESB | NI | GU_500041 | CGT8 | Coolkeeragh OCGT |  | Gasoil | 100% |  |  | Gasoil | 8 | 53 |  | 180 | 53 |  |  |  |  | 11.05 |  |  |  |  | 2.4% | 176 | 50 | 50 | 0.5 | 0.5 | 8 | 8 | 8 | 0.5 | 0.5
Contour | NI | GU_500904 | Contour AGU | Contour Global Agg Unit |  | Gas | 100% |  |  | Gas | 6 | 12.084 |  | 15.408 | 9 | 12 |  |  |  | 7.632 | 8.316 |  |  |  | 6.2% | 48 | 4.032 | 4.032 | 0.5 | 0.5 | 0.616 | 0.616 | 0.616
ESB | NI | GU_500040 | CPS CCGT | Coolkeeragh CCGT |  | Gas | 100% |  |  | Gas | 260 | 404 |  | 633.8 | 260 | 328 | 372 | 404 |  | 4.384 | 5.341 | 5.573 | 5.603 |  | 6.2% | 176 | 15 | 15 | 4 | 4 | 1088 | 1088 | 1088 | 12 | 60
ESB | ROI | GU_400500 | DB1 | Dublin Bay CCGT |  | Gas | 100% |  |  | Gas | 130 | 415 |  | 666 | 130 | 415 |  |  |  | 4.053 | 6.05 |  |  |  | 6.2% | 167 | 10 | 4.48 | 4 | 1 | 2600 | 2600 | 2600 | 12 | 60
Covanta | ROI | GU_402030 | Dublin | Dublin |  | Gasoil | 100% |  |  | Waste | 21.4 | 68.2 | 67.6 | [11 empty] | 6.7% | 36 | 0.9 | 0.9 |  |  | 1279.3 | 1827.5 |  | 24 | >24
BnM | ROI | GU_401860 | ED1 | Edenderry |  | GasOil | 100% |  |  | Peat | 41 | 117.57 |  | 497.6 | 88 | 112 | 118 |  |  | 3.93 | 8.95 | 8.95 |  |  | 7.9% | 72 | 1.76 | 1.76 | 4 | 0.5 | 436 | 1084 | 2308 | 12 | 48
BnM | ROI | GU_401010 | ED3 | Cushaling |  | GasOil | 100% |  |  | GasOil | 20 | 58 |  | 85 | 58 |  |  |  |  | 9.5 |  |  |  |  | 2.4% | 24 | 5 | 5 |  | 0.5 | 22
BnM | ROI | GU_401011 | ED5 | Cushaling |  | GasOil | 100% |  |  | GasOil | 20 | 58 |  | 85 | 58 |  |  |  |  | 9.5 |  |  |  |  | 2.4% | 24 | 5 | 5 |  | 0.5 | 22
ESB | ROI | GU_400210 | ER1 | Erne 1 |  | Water | 100% |  |  | Water |  | 10 | [12 empty] | 4.5% | 86 | 5 | 10
ESB | ROI | GU_400211 | ER2 | Erne 2 |  | Water | 100% |  |  | Water |  | 10 | [12 empty] | 4.5% | 86 | 5 | 10
ESB | ROI | GU_400220 | ER3 | Erne 3 |  | Water | 100% |  |  | Water |  | 22.5 | [12 empty] | 4.5% | 83 | 10 | 22.5
ESB | ROI | GU_400221 | ER4 | Erne 4 |  | Water | 100% |  |  | Water |  | 22.5 | [12 empty] | 4.5% | 86 | 10 | 22.5
SSE | ROI | GU_400762 | GI CCGT | Great Island CCGT |  | Gas | 100% | 0 | 0 | Gas | 165 | 464 | 458.5 | 605 | 165 | 431 | 464 | 0 | 0 | 4.07 | 5.46 | 5.69 | 0 | 0 | 5% | 55 | 17.17 | 18.5 | 4 | 4 | 630 | 1700 | 2650 | 12 | 60
Energia Generation | ROI | GU_400540 | HN2 | Huntstown Phase II | 2019-10-01 | Gas | 100% |  |  | Gas | 121 | 404 | 391.88 | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 6.2% | 55 | 20 | 20 | 4 | 4 | 318.454 | 531.129 | 644.171 | 12 | 60
Energia Generation | ROI | GU_400540 | HN2 | Huntstown Phase II | 2021-01-01 | Gas | 100% |  |  | Gas | 121 | 404 | 391.88 | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 6.2% | 55 | 20 | 20 | 4 | 4 | 318.454 | 531.129 | 644.171 | 12 | 60
Energia Generation | ROI | GU_400540 | HN2 | Huntstown Phase II | 2021-10-01 | Gas | 100% |  |  | Gas | 121 | 404 | 391.88 | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 6.2% | 55 | 20 | 20 | 4 | 4 | 318.454 | 531.129 | 644.171 | 12 | 60
Energia Generation | ROI | GU_400540 | HN2 | Huntstown Phase II | 2022-10-01 | Gas | 100% |  |  | Gas | 121 | 404 | 391.88 | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 6.2% | 55 | 20 | 20 | 4 | 4 | 318.454 | 531.129 | 644.171 | 12 | 60
Energia Generation | ROI | GU_400540 | HN2 | Huntstown Phase II | 2023-10-01 | Gas | 100% |  |  | Gas | 121 | 404 | 391.88 | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 6.2% | 55 | 20 | 20 | 4 | 4 | 318.454 | 531.129 | 644.171 | 12 | 60
Energia Generation | ROI | GU_400540 | HN2 | Huntstown Phase II | 2024-05-01 | Gas | 100% |  |  | Gas | 121 | 404 | 391.88 | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 6.2% | 55 | 20 | 20 | 4 | 4 | 318.454 | 531.129 | 644.171 | 12 | 60
Energia Generation | ROI | GU_400480 | HNC | Huntstown | 2019-10-01 | Gas | 100% |  |  | Gas | 120 | 343 | 332.71 | 541.204 | 120 | 171 | 230 | 250 | 352 | 4.528 | 4.53 | 5.237 | 5.247 | 6.039 | 6.2% | 55 | 7 | 7 | 4 | 4 | 834.687 | 2803.196 | 4771.682 | 12 | 60
Energia Generation | ROI | GU_400480 | HNC | Huntstown | 2019-09-01 | Gas | 100% |  |  | Gas | 120 | 343 | 332.71 | 541.204 | 120 | 171 | 230 | 250 | 352 | 4.528 | 4.53 | 5.237 | 5.247 | 6.039 | 6.2% | 55 | 7 | 7 | 4 | 4 | 834.687 | 2803.196 | 4771.682 | 12 | 60
iPower | NI | GU_501130 | iPower AGU | iPower AGU |  | Gasoil | 100% |  |  | Gasoil |  | 64 |  | 42.943 |  | 64 |  |  |  | 10.7266 | 10.7266 |  |  |  | 2.4% | 48 | 8 | 8 | 0.5 | 0.5 | 32.1799
Indaver | ROI | GU_401230 | IW1 | Indaver Energy Limited | [5 empty] | Waste | 1 | 17 | [12 empty] | 6.6% | 2.2 | 0.36 | 0.65
EP | NI | GU_500822 | K1 Coal 220 | Kilroot Unit 1 FGD |  | Oil | 80% | Coal | 20% | Coal | 93 | 255.26 |  | 393.61 | 93 | 174.8 | 255.26 |  |  | 9.4 | 9.4 | 71.5 |  |  | 6% | 72 | 5.79 | 5.79 | 4 | 0.5 | 1984 | 4281 | 5054 | 7.5 | 52.5
EP | NI | GU_500823 | K2 Coal 220 | Kilroot Unit 2 FGD |  | Oil | 80% | Coal | 20% | Coal | 93 | 257.92 |  | 393.61 | 93 | 174.8 | 257.92 |  |  | 9.4 | 9.4 | 69.49 |  |  | 6% | 72 | 5.79 | 5.79 | 4 | 0.5 | 1984 | 4281 | 5054 | 7.5 | 52.5
EP | NI | GU_500824 | KGT1 | Kilroot GT1 |  | Gasoil | 100% |  |  | Gasoil | 5 | 29 |  | 103 | 5 | 23.6 | 29.2 |  |  | 11.05 | 11.05 | 11.05 |  |  | 2% | 24 | 6 | 6 | 0.02 | 0.25 | 8 | 8 | 8
EP | NI | GU_500825 | KGT2 | Kilroot GT2 |  | Gasoil | 100% |  |  | Gasoil | 5 | 29 |  | 103 | 5 | 23.6 | 29.2 |  |  | 11.05 | 11.05 | 11.05 |  |  | 2% | 24 | 6 | 6 | 0.02 | 0.25 | 8 | 8 | 8
EP | NI | GU_500820 | KGT3 | Kilroot GT3 |  | Gasoil | 100% |  |  | Gasoil | 12.82 | 42 |  | 115.39 | 12.82 | 41.61 |  |  |  | 9.2356 | 9.2356 |  |  |  | 2% | 24 | 10 | 10 | 0.62 | 0.38 | 9.55 | 9.55 | 9.55
EP | NI | GU_500821 | KGT4 | Kilroot GT4 |  | Gasoil | 100% |  |  | Gasoil | 12.82 | 42 |  | 115.39 | 12.82 | 41.61 |  |  |  | 9.2356 | 9.2356 |  |  |  | 2% | 24 | 10 | 10 | 0.62 | 0.38 | 9.55 | 9.55 | 9.55
ESB | ROI | GU_400280 | LE1 | Lee 1 |  | Water | 100% |  |  | Water |  | 15 | [12 empty] | 4.5% | 123 | 2.4 | 15
ESB | ROI | GU_400281 | LE2 | Lee 2 |  | Water | 100% |  |  | Water |  | 4 | [12 empty] | 4.5% | 123 | 0.6 | 4
ESB | ROI | GU_400290 | LE3 | Lee 3 |  | Water | 100% |  |  | Water |  | 8 | [12 empty] | 4.5% | 83 | 1.5 | 8
ESB | ROI | GU_400250 | LI1 | Liffey 1 |  | Water | 100% |  |  | Water |  | 15 | [12 empty] | 4.5% | 130 | 5 | 10
ESB | ROI | GU_400251 | LI2 | Liffey 2 |  | Water | 100% |  |  | Water |  | 15 | [12 empty] | 4.5% | 130 | 5 | 10
ESB | ROI | GU_400252 | LI4 | Liffey 4 |  | Water | 100% |  |  | Water |  | 4 | [12 empty] | 4.5% | 90 | 2 | 2
ESB | ROI | GU_400260 | LI5 | Liffey 5 |  | Water | 100% |  |  | Water |  | 4 | [12 empty] | 4.5% | 130 | 0.03 | 0.1
Evermore Energy | NI | GU_501350 | Lisahally | Lisahally / Maydown |  | LSFO | 100% |  |  | Waste wood | 12.74 | 17.6 |  | 40 | 17.6 |  |  |  |  | 9 | [6 empty] | 0.04 | 0.04 | 4 | 0.5 | 2000 | 4000 | 6000 | 2 | 4
ESB | ROI | GU_400240 | LR4 | Lough Ree |  | Peat | 100% |  |  | Peat | 32 | 93 |  | 86.8 | 91 | 93 |  |  |  | 8.811 | 8.811 |  |  |  | 7.9% | 339 | 0.44 | 0.44 | 1 | 4 | 300 | 300 | 300 | 12 | 48
ESB | ROI | GU_400270 | MP1 | Moneypoint 1 |  | Coal | 68% | Oil | 32% | Coal | 75 | 285 |  | 215.4 | 75 | 140 | 195 | 280 | 285 | 8.906 | 8.99 | 9.192 | 9.242 | 13.696 | 9.1% | 284 | 1.63 | 1.33 | 6 | 5 | 4360 | 4360 | 4360 | 12 | 60
ESB | ROI | GU_400271 | MP2 | Moneypoint 2 |  | Coal | 68% | Oil | 32% | Coal | 99 | 285 |  | 215.4 | 99 | 140 | 195 | 280 | 285 | 8.937 | 8.966 | 9.192 | 9.242 | 13.696 | 9.1% | 283 | 1.63 | 1.33 | 6 | 5 | 4360 | 4360 | 4360 | 12 | 60
ESB | ROI | GU_400272 | MP3 | Moneypoint 3 |  | Coal | 68% | Oil | 32% | Coal | 75 | 285 |  | 215.4 | 75 | 140 | 195 | 280 | 285 | 8.906 | 8.99 | 9.192 | 9.242 | 13.696 | 9.1% | 284 | 1.63 | 1.33 | 6 | 5 | 4360 | 4360 | 4360 | 12 | 60
ESB | ROI | GU_403680 | n_CDF |  | 2022-10-01 | Gas | 100% |  |  | Gas | 27.5 | 70 |  |  | 27.5 | 70 |  |  |  | 8.78 |  |  |  |  | 6.2% | [5 empty] | 50 | 50 | 50
ESB | ROI | GU_403650 | n_NW4 | northwall 4 GT | 2022-10-01 | Gas | 100% |  |  | Gas | 42 | 118 |  | 300 | 42 | 118 |  |  |  | 9.47 |  |  |  |  | 6.2% |  | 30 | 30 | 1 | 1 | 100 | 100 | 100 | 4 | 12
ESB | ROI | GU_400311 | n_NW5 | North Wall 5 refurb | 2022-10-01 | Gas | 100% |  |  | Gas | 42 | 118 |  | 300 | 42 | 118 |  |  |  | 9.47 |  |  |  |  | 6.2% |  | 30 | 30 | 1 | 1 | 100 | 100 | 100 | 4 | 12
ESB | ROI | GU_403620 | n_PB |  | 2022-10-01 | Gas | 100% |  |  | Gas | 27.5 | 70 |  |  | 27.5 | 70 |  |  |  | 8.78 |  |  |  |  | 6.2% | [5 empty] | 50 | 50 | 50
ESB | ROI | GU_403610 | n_RNS |  | 2022-10-01 | Gas | 100% |  |  | Gas | 27.5 | 70 |  |  | 27.5 | 70 |  |  |  | 8.78 |  |  |  |  | 6.2% | [5 empty] | 50 | 50 | 50
ESB | ROI | GU_400311 | NW5 | North Wall 5 |  | Gas | 100% |  |  | Gas | 19 | 109 |  | 318.8 | 50 | 109 |  |  |  | 8.627 | 9.272 |  |  |  | 6.2% | 328 | 8 | 5.82 | 1 | 1 | 50 | 50 | 50 | 12 | 48
ESB | ROI | GU_400324 | PBA | Poolbeg C_A |  | Gas | 100% |  |  | Gas | 120 | 255 |  | 352.9 | 145 | 240 | 255 |  |  | 5.435 | 6.057 | 7.007 |  |  | 6.2% | 154 | 5 | 5 | 1 | 1 | 750 | 750 | 750 | 12 | 48
ESB | ROI | GU_400325 | PBB | Poolbeg C_B |  | Gas | 100% |  |  | Gas | 120 | 255 |  | 352.9 | 145 | 240 | 255 |  |  | 5.435 | 6.057 | 7.007 |  |  | 6.2% | 154 | 5 | 5 | 1 | 1 | 750 | 750 | 750 | 12 | 48
SSE | ROI | GU_400770 | RH1 | Rhode 1 |  | Gasoil | 100% | 0 | 0 | Gasoil | 5 | 52 | 0 | 85.01 | 12 | 52 | 0 | 0 | 0 | 9.8226 | 9.8226 | 0 | 0 | 0 | 2.4% | 50 | 10 | 10 | 0 | 0.75 | 24 | 0 | 0 | 0 | 0
SSE | ROI | GU_400771 | RH2 | Rhode 2 |  | Gasoil | 100% | 0 | 0 | Gasoil | 5 | 52 | 0 | 85.01 | 12 | 52 | 0 | 0 | 0 | 9.8226 | 9.8226 | 0 | 0 | 0 | 2.4% | 50 | 10 | 10 | 0 | 0.75 | 24 | 0 | 0 | 0 | 0
Aughinish | ROI | GU_400120 | SK3 | Sealrock 3 (Aughinish CHP) |  | Gas | 100% |  |  | Gas | 40 | 83 |  | 100 | 40 | 83 |  |  |  | 5 | 5 |  |  |  | 1% | 44 | 6 | 6 | 4 | 4 | 800 | 1000 | 1200 | 12 | 48
Aughinish | ROI | GU_400121 | SK4 | Sealrock 4 (Aughinish CHP) |  | Gas | 100% |  |  | Gas | 40 | 83 |  | 100 | 40 | 83 |  |  |  | 5 | 5 |  |  |  | 1% | 44 | 6 | 6 | 4 | 4 | 800 | 1000 | 1200 | 12 | 48
SSE | ROI | GU_400750 | TB1 | Tarbert Unit 1 |  | Oil | 61% | Gasoil | 39% | Oil | 18 | 54 | 0 | 44.66 | 20 | 46 | 54 | 0 | 0 | 11.63 | 11.63 | 11.75 | 0 | 0 | 2% | 50 | 1 | 1 | 2 | 2 | 217.5 | 449 | 562 | 12 | 48
SSE | ROI | GU_400751 | TB2 | Tarbert Unit 2 |  | Oil | 61% | Gasoil | 39% | Oil | 18 | 54 | 0 | 44.66 | 20 | 46 | 54 | 0 | 0 | 11.63 | 11.63 | 11.75 | 0 | 0 | 2% | 50 | 1 | 1 | 2 | 2 | 217.5 | 449 | 562 | 12 | 48
SSE | ROI | GU_400752 | TB3 | Tarbert Unit 3 |  | Oil | 70% | Gasoil | 30% | Oil | 34.85 | 243 | 0 | 247.61 | 34.85 | 100 | 180 | 240 | 0 | 8.0698 | 8.0698 | 9.063 | 9.153 | 0 | 2% | 50 | 2 | 2.2 | 4 | 4 | 1072 | 1934 | 3180 | 14 | 106
SSE | ROI | GU_400753 | TB4 | Tarbert Unit 4 |  | Oil | 70% | Gasoil | 30% | Oil | 34.85 | 243 | 0 | 247.61 | 34.85 | 100 | 180 | 240 | 0 | 8.4 | 8.4 | 9.428 | 9.64 | 0 | 2% | 50 | 2 | 2.2 | 4 | 4 | 1072 | 1934 | 3180 | 14 | 106
ESB | ROI | GU_400360 | TH1 | Turlough Hill 1 |  | Water | 100% |  |  | Water |  | 73 | [12 empty] | 6% | 123
ESB | ROI | GU_400361 | TH2 | Turlough Hill 2 |  | Water | 100% |  |  | Water |  | 73 | [12 empty] | 6% | 123
ESB | ROI | GU_400362 | TH3 | Turlough Hill 3 |  | Water | 100% |  |  | Water |  | 73 | [12 empty] | 6% | 123
ESB | ROI | GU_400363 | TH4 | Turlough Hill 4 |  | Water | 100% |  |  | Water |  | 73 | [12 empty] | 6% | 123
SSE | ROI | GU_400780 | TP1 | Tawnaghmore 1 |  | Gasoil | 100% | 0 | 0 | Gasoil | 5 | 52 | 0 | 86.62 | 12 | 52 | 0 | 0 | 0 | 9.5867 | 9.5867 | 0 | 0 | 0 | 2.4% | 123 | 10 | 10 | 0 | 0.75 | 24 | 0 | 0 | 0 | 0
SSE | ROI | GU_400781 | TP3 | Tawnaghmore 3 |  | Gasoil | 100% | 0 | 0 | Gasoil | 5 | 52 | 0 | 86.62 | 12 | 52 | 0 | 0 | 0 | 9.5867 | 9.5867 | 0 | 0 | 0 | 2.4% | 50 | 10 | 10 | 0 | 0.75 | 24 | 0 | 0 | 0 | 0
Tynagh Energy Limited | ROI | GU_400530 | TY | Tynagh |  | Gas | 100% |  |  | Gas | 194 | 404 |  | 594 | 194 | 200 | 280 | 320 | 404 | 4.7297 | 5.0739 | 5.1158 | 5.5018 | 5.9738 | 6.2% | 64.5 | 15 | 12.5 | 4 | 4 | 1200 | 2000 | 3000 | 12 | 48
BGE | ROI | GU_400930 | WG | Whitegate |  | Gas | 100% |  |  | Gas | 160 | 445 | 432 | 666.7 | 185 | 399 | 460 |  |  | 3.91 | 5.265 | 5.265 |  |  | 6.2% | 32.1 | 20.6 | 26.8 | 4 | 4 | 222.6 | 329.9 | 437.1 | 12 | 60
ESB | ROI | GU_400370 | WO4 | West Offaly |  | Peat | 100% |  |  | Peat | 48 | 140 |  | 120.5 | 137 | 140 |  |  |  | 8.659 | 8.659 |  |  |  | 7.9% | 339 | 0.7 | 0.7 | 1 | 4 | 450 | 450 | 450 | 12 | 60
ESB | ROI | GU_403560 |  |  | 2022-10-01 |  | 100% |  |  |  |  | 19
ESB | ROI | GU_403600 |  |  | 2022-10-01 |  | 100% |  |  |  |  | 30
ESB | ROI | GU_403630 |  |  | 2022-10-01 |  | 100% |  |  |  |  | 75
ESB | ROI | GU_403660 |  |  | 2022-10-01 |  | 100% |  |  |  |  | 30

## power flow
Table H-1 Power Flows, Summer Valley and Winter Peak 2021 and 2030
|  |  |  | 2021 | [5 empty] | 2030
Line |  |  |  | Summer Valley |  |  | Winter Peak |  |  | Summer Valley |  |  | Winter Peak
From | To | kV | No. | MW | MVAR | % | MW | MVAR | % | MW | MVAR | % | MW | MVAR | %
DSN | CNB | 400 | 1 | - | - | - | - | - | - | -187.7 | -44.8 | 12.2 | -213.9 | -12.2 | 11
KPG | MP | 400 | 1 | - | - | - | - | - | - | 166.3 | -18.2 | 13.8 | 228.7 | -16.3 | 19
CNB | MP | 400 | 1 | - | - | - | - | - | - | -222.7 | -99.4 | 15.5 | -271.7 | -90.8 | 14.7
MP | OST | 400 | 1 | 35.2 | 30.3 | 4.7 | 204.1 | -6.3 | 20.5 | 39 | 27.1 | 4.8 | 104.7 | 54.7 | 11.9
OST | WOO | 400 | 1 | -39.4 | 153 | 15.8 | 237.3 | 72 | 24.9 | 277 | 25.8 | 27.9 | 282.5 | 175.8 | 33.4
WOO | PRT | 400 | 1 | -199.9 | 173.3 | 38.6 | -419.8 | -118.1 | 63.7 | -200 | 63.5 | 30.6 | -499.8 | 71.3 | 73.7
WOO | TUR | 400 | 1 | - | - | - | - | - | - | -81.3 | -41.8 | 6.4 | 378.7 | -41.3 | 22
LOU | TAN | 275 | 1 | 108.3 | -15.2 | 15.4 | 437.9 | -10.7 | 49.7 | -120.3 | 0.2 | 16.9 | 57 | 11.4 | 6.6
LOU | TAN | 275 | 2 | 108.2 | -16.4 | 15.4 | 438.1 | -34 | 49.9 | -120.4 | 1.5 | 17 | 57.2 | 10.8 | 6.6
BPS | HAN | 275 | 2 | -14.8 | -16.4 | 3.1 | 39.4 | 23.4 | 5.2 | 119.9 | 1.1 | 16.9 | 167.5 | -0.6 | 19
BPS | KEL | 275 | 1 | -131.9 | 10.7 | 18.6 | -176.4 | 78.4 | 21.9 | 115.2 | 32.5 | 16.9 | 27.4 | 46.2 | 6.1
BPS | MAG | 275 | 1 | -92.3 | -7 | 13 | -147 | 36.6 | 17.2 | 73.1 | 15.2 | 10.5 | 27 | 9.6 | 3.3
BPS | BYC | 275 | 1 | 280.6 | 32.6 | 39.8 | 433.5 | -57.2 | 49.6 | 41.5 | -31.5 | 7.3 | 89 | -31.3 | 10.7
CAS | HAN | 275 | 1 | 34.9 | -6.7 | 5 | 45.5 | -46.9 | 7.4 | -74.7 | -29.7 | 11.3 | -90.2 | -18.7 | 10.5
CAS | HAN | 275 | 2 | 34.9 | -6.7 | 5 | 45.5 | -46.9 | 7.4 | -74.7 | -29.7 | 11.3 | -90.2 | -18.7 | 10.5
CAS | KPS | 275 | 1 | -74 | 6.4 | 10.5 | -148.5 | 17.3 | 17 | -24.5 | -4.4 | 3.5 | -155.6 | 20.7 | 17.8
CAS | TAN | 275 | 1 | -100 | 22.7 | 14.4 | -304.9 | 67.3 | 35.4 | 68.6 | 29.5 | 10.5 | -112.9 | 24.6 | 13.1
CPS | CPS | 275 | 1 | 86.2 | -17.4 | 11.6 | 90 | -5.8 | 10.8 | 62.4 | -26.3 | 8.9 | -19.4 | -14 | 2.9
CPS | CPS | 275 | 1 | 86.2 | -17.4 | 11.6 | 90 | -5.8 | 10.8 | 62.4 | -26.3 | 8.9 | -19.4 | -13.4 | 2.8
CPS | MAG | 275 | 1 | 86.2 | -13.1 | 21.2 | 90 | -1.6 | 17.5 | 62.4 | -22.3 | 8.7 | -19.4 | -9.8 | 2.6
CPS | MAG | 275 | 2 | 86.2 | -13.1 | 21.2 | 90 | -1.6 | 17.5 | 62.4 | -22.3 | 8.7 | -19.4 | -9.8 | 2.6
HAN | BYC | 275 | 1 | 20.1 | 5.1 | 2.9 | -32.3 | -36.4 | 5.5 | -121 | -10.6 | 17.1 | -168.3 | -7 | 19.1
KEL | KPS | 275 | 1 | -58.6 | 0.1 | 8.3 | -103 | 29.3 | 12.2 | 41.8 | -10.6 | 6.1 | -74 | 12.2 | 8.5
KEL | KPS | 275 | 2 | -58.6 | 0.1 | 8.3 | -103 | 29.3 | 12.2 | 41.8 | -10.6 | 6.1 | -74 | 12.2 | 8.5
KEL | MAG | 275 | 1 | -47.9 | -18 | 7.2 | -113.1 | -3.4 | 12.8 | 26 | 4.7 | 3.7 | 26.1 | -21.5 | 3.8
KPS | TAN | 275 | 1 | 4.5 | -7.6 | 1.3 | -50.4 | 7.1 | 5.8 | 58.9 | 6.4 | 8.4 | 64.8 | -15.2 | 7.6
MAG | TMN | 275 | 1 | 15.5 | 1.5 | 2.2 | -40.9 | 38.2 | 6.4 | 111.8 | 12.7 | 15.8 | 7.2 | 11.8 | 1.6
MAG | TMN | 275 | 2 | 15.5 | 1.5 | 2.2 | -40.9 | 38.2 | 6.4 | 111.8 | 12.7 | 15.8 | 7.2 | 11.8 | 1.6
TAN | TUR | 275 | 1 | - | - | - | - | - | - | -77 | -22.7 | 11.3 | -119.9 | -7.7 | 13.6
TAN | TUR | 275 | 2 | - | - | - | - | - | - | -77 | -22.7 | 11.3 | -119.9 | -7.7 | 13.6
TMN | TUR | 275 | 1 | - | - | - | - | - | - | 117.9 | 3.8 | 16.6 | -67.5 | 12.9 | 7.8
TMN | TUR | 275 | 2 | - | - | - | - | - | - | 117.9 | 3.8 | 16.6 | -67.5 | 12.9 | 7.8
AD | AD | 220 | 1 | 39.7 | -23.7 | 7.8 | 42.5 | -99.2 | 18.2 | -139.2 | 52.9 | 25.1 | 137.1 | -115 | 30.2
AD | AD | 220 | 1 | 39.7 | -23.7 | 7.8 | 42.5 | -99.2 | 18.2 | -139.2 | 52.9 | 25.1 | 69.4 | 4.9 | 11.7
AD | KRA | 220 | 1 | 96.9 | -87.6 | 33.2 | 167.6 | 9.4 | 35.9 | 79.7 | -20.7 | 21 | 239 | 16.6 | 51.2
AD | RAF | 220 | 1 | 62.5 | -70.6 | 21.7 | 121.8 | -10.6 | 23.8 | 35.9 | -25.8 | 10.2 | 169 | -20.4 | 33.2
AD | AD | 220 | 1 | 39.7 | -23.7 | 7.8 | 42.5 | -99.2 | 18.2 | -139.2 | 52.9 | 25.1 | -455.7 | 102.5 | 78.8
AD | GGO | 220 | 1 | -55.9 | 62.4 | 14.6 | -122.8 | 10.5 | 21.5 | -217.8 | 73.1 | 40.1 | -98.4 | -131.8 | 28.7
AD | KRA | 220 | 2 | 95.7 | -86.1 | 32.8 | 165.1 | 9.6 | 35.3 | 78.6 | -20.2 | 20.7 | 235.5 | 16.8 | 50.5
ARK | CKM | 220 | 1 | 36.4 | -6.4 | 8.5 | 98.3 | -20.9 | 19.6 | 130 | -18.1 | 30.2 | 236.3 | -81.1 | 48.7
ARK | LWD | 220 | 1 | -54.6 | 8.5 | 12.7 | -135.5 | 6.5 | 31.2 | -134.4 | 15.4 | 31.2 | -277.9 | 76.4 | 66.3
BVK | CLA | 220 | 1 | -69 | 175.1 | 25.4 | 67.2 | -3.2 | 8.5 | -14 | 5.5 | 2 | -116 | 36.6 | 15.4
BVK | BYH | 220 | 1 | 69 | -99.7 | 27.9 | 33.7 | -23.7 | 5.2 | 86.9 | -28.6 | 12 | 216.8 | -39.6 | 27.8
BLC | FIN (I) | 220 | 1 | -52.5 | 11.3 | 9.4 | -109.6 | -13.1 | 19.4 | -66 | 68.6 | 16.7 | -34.8 | -18.9 | 7
BLC | SHL | 220 | 1 | - | - | - | - | - | - | -35.4 | -71.8 | 14 | -145.7 | -16.5 | 25.7
CLE | CDU | 220 | 1 | -5.3 | -1.4 | 1.3 | 51.2 | -54.5 | 14.6 | 148.8 | -88.4 | 39.9 | -93.6 | -47.6 | 20.5
CLE | WOO | 220 | 1 | -67.7 | -8.6 | 15.7 | -124.1 | 46.9 | 25.9 | -288.9 | 46.2 | 67.4 | -45.7 | 10.4 | 9.1
CLE | BTN | 220 | 1 | 0 | -8.5 | 1.5 | 0 | -9.6 | 1.7 | 0 | -8.2 | 1.4 | 0 | -9.5 | 1.7
CLE | BTN | 220 | 2 | 0 | -8.5 | 1.5 | 0 | -9.6 | 1.7 | 0 | -8.2 | 1.4 | 0 | -9.5 | 1.7
CLA | KRA | 220 | 1 | -97.3 | 155.1 | 28.3 | -15.1 | -20 | 3.3 | -5.4 | 7 | 1.4 | -163.5 | 15.9 | 21.9
CSH | FLA | 220 | 1 | 60.7 | 11.6 | 17.7 | 232.6 | 17.5 | 53.5 | 46.9 | -10 | 13.7 | 153 | 3.3 | 35.1
CSH | PRO | 220 | 1 | -58 | -4.5 | 14.8 | -165.3 | 9.8 | 35.4 | 19.2 | -24.1 | 7.9 | -86.5 | -0.8 | 18.5
CSH | TYN | 220 | 1 | -73.9 | 63.3 | 12.8 | -239.1 | 3.6 | 30.2 | -95.4 | 48.3 | 14.1 | -201.4 | -1.1 | 25.4
CKM | DSN | 220 | 1 | -95.9 | -8.3 | 22.2 | -127.6 | 58 | 27.3 | -211.3 | 25.6 | 49 | -70.9 | 47.4 | 16.6
CKM | ISH | 220 | 1 | 140.7 | -63 | 26 | 98.3 | -219.2 | 40.5 | 204.8 | -32 | 35 | -10.5 | -196.8 | 33.2
CKM | CKM | 220 | 1 | -89.6 | -19.7 | 26.2 | -97.7 | -10.8 | 28.1 | 62.3 | -10.2 | 18.1 | 104.7 | -8.2 | 30
CUL | GI | 220 | 1 | -51 | 54.7 | 10 | 11.9 | -33.1 | 4.4 | 52.5 | -7 | 7.1 | -108.6 | 44.2 | 14.8
CUL | KRA | 220 | 1 | 1.6 | -31.5 | 4.9 | -123.6 | 20 | 16.4 | -85.6 | 7.9 | 13.3 | -40.3 | -46.3 | 8
CDU | CRH | 220 | 1 | - | - | - | 1.9 | -4.2 | 0.8 | 25.4 | 4.6 | 4.5 | 25.4 | 3.9 | 4.5
CDU | CRH | 220 | 2 | - | - | - | 1.9 | -4.2 | 0.8 | 25.4 | 4.6 | 4.5 | 25.4 | 3.9 | 4.5
CDU | FIN (I) | 220 | 1 | 54.1 | -89.4 | 24.1 | 20.8 | -0.2 | 4.1 | 127.5 | -109.1 | 38.7 | -23 | 6.6 | 4.7
CDU | HN | 220 | 1 | -219.5 | 185.9 | 51.8 | -219.4 | -218.7 | 55.8 | 0 | -13.3 | 2.4 | -398.8 | -206.1 | 80.9
CDU | FIN (I) | 220 | 2 | 54.1 | -89.4 | 24.1 | 20.8 | -0.2 | 4.1 | 127.5 | -109.1 | 38.7 | -23 | 6.6 | 4.7
CDU | WOO | 220 | 2 | -49.6 | -6.8 | 11.5 | -108.3 | 50.4 | 23.3 | -260.8 | 61.1 | 61.7 | -8.1 | 20.7 | 4.3
DSN | KLS | 220 | 1 | -0.8 | 7 | 1.8 | -32.5 | 3.8 | 7 | -66.8 | 17.8 | 17.6 | -211.7 | 101.6 | 50.2
DSN | MAY | 220 | 1 | 101.8 | -17.1 | 29.5 | 247.7 | -2.2 | 56.8 | 130.6 | 4.5 | 30.1 | 176.4 | -11.4 | 34.5
DSN | MAY | 220 | 2 | 198.4 | -31.8 | 57.4 | 274.6 | -52.9 | 64.2 | 130.6 | 4.5 | 30.1 | 176.4 | -11.4 | 34.5
DSN | TH | 220 | 1 | -494 | 165.9 | 148.5 | -376.8 | 113.1 | 112.1 | -220.3 | 32.5 | 63.5 | 1.4 | -15.5 | 4.4
FLA | LOU | 220 | 1 | -0.2 | 57.9 | 15.1 | 169.7 | 21.1 | 36 | 56.4 | 0.8 | 14.7 | 49.8 | 8 | 10.6
FLA | SRA | 220 | 1 | 31.1 | -27.8 | 9.6 | 3.3 | -15.1 | 3 | -23.1 | -1.8 | 5.3 | 36.5 | -10.6 | 7.4
FIN (I) | HN | 220 | 1 | 0 | -4 | 0.7 | -336.8 | 36.4 | 57.1 | 0 | -3.8 | 0.7 | -352 | -4.6 | 59.4
FIN (I) | NW | 220 | 1 | -24.3 | -56.5 | 18.5 | -80 | -42.8 | 27.3 | -0.4 | -97.4 | 29.3 | -159.5 | -27.4 | 48.7
GI | KLS | 220 | 1 | 51.8 | -29.3 | 15.1 | 157.4 | 24.7 | 34 | 74 | -5.3 | 18.9 | 326.6 | -8.7 | 69.8
GI | LWD | 220 | 1 | 75.2 | -37.5 | 19.4 | 168.8 | -2.7 | 32.9 | 124.1 | -16.7 | 28.9 | 330.8 | -43.5 | 65
GI | LWN | 220 | 1 | - | - | - | - | - | - | -180 | 22 | 30.6 | -499.7 | 306.1 | 98.8
GOR | LOU | 220 | 1 | 128.3 | -42.6 | 31.2 | 307.7 | 7.1 | 64.7 | -93.1 | 7.6 | 21.5 | 44.9 | 6.2 | 9.5
GOR | MAY | 220 | 1 | -192.7 | 67.4 | 58.3 | -409.4 | -6.6 | 93.9 | 40.8 | -5.1 | 11.8 | -179.1 | -19.9 | 41.3
GGO | RAF | 220 | 1 | 141.6 | -141.8 | 35.2 | 265.4 | -5.5 | 46.6 | 137.4 | -60.5 | 26.3 | 344.9 | 24.5 | 60.7
INC | ISH | 220 | 1 | -356.9 | 122.4 | 67.1 | -782.3 | -78.6 | 124 | -204.5 | -33 | 36.9 | -735.1 | -176.4 | 119.2
INC | CBT | 220 | 2 | -58 | 5.7 | 7.7 | -12.9 | 91.2 | 11.6 | -66.7 | 87.4 | 14.5 | 59.9 | 89.5 | 13.6
ISH | SHL | 220 | 1 | 0 | -3.7 | 0.7 | -312.7 | -37.2 | 57.5 | 0 | -3.6 | 0.7 | -312.7 | -103.8 | 60.1
KNR | BYH | 220 | 1 | -68.3 | 9.8 | 15.9 | -125.3 | 49 | 17 | -144.7 | 57.5 | 21 | -304.5 | 69.3 | 39.4
KNR | KPG | 220 | 1 | 27.5 | 2 | 3.8 | 77.7 | -22.6 | 10.6 | 77.4 | -42 | 12.1 | 147.5 | -36.3 | 19.9
KNR | KPG | 220 | 2 | 40.7 | -46.8 | 8.5 | 122.4 | -69.1 | 18.4 | 126.2 | -93.5 | 21.5 | 231.7 | -74.4 | 31.9
KRA | KLN | 220 | 1 | 113.5 | -94.7 | 28.9 | 156.4 | 0.9 | 27.7 | 88.5 | -28.4 | 18.2 | 274.5 | -17.1 | 48.8
KRA | RAF | 220 | 1 | -93 | 82.6 | 35.2 | -152.6 | -10.3 | 33.7 | -84.8 | 17.7 | 24.6 | -220.2 | -20.2 | 48.7
KLN | SH | 220 | 1 | 22.1 | -1 | 8.2 | 138.7 | -16.7 | 39.5 | 89.6 | -14.8 | 33.8 | 135.8 | -20.1 | 38.8
KLN | KPG | 220 | 1 | 5.1 | -80.9 | 18.7 | -92.8 | -35.8 | 19.4 | 18.1 | -32.9 | 8.7 | 56.7 | -44.4 | 14.1
KYT | MAY | 220 | 1 | - | - | - | - | - | - | 14.9 | -14.2 | 2.7 | 73.6 | 31.4 | 10.7
KYT | WOO | 220 | 1 | - | - | - | - | - | - | -132 | -29.6 | 17.8 | -190.6 | -74.4 | 27.4
KPG | MP | 220 | 1 | -7.5 | 11.7 | 2.1 | -56.6 | -47.7 | 11.2 | 34.3 | -28 | 6.7 | 92 | -27 | 14.5
KPG | MP | 220 | 2 | -7.5 | 11.7 | 2.1 | -56.6 | -47.7 | 11.2 | 34.3 | -28 | 6.7 | 92 | -27 | 14.5
KPG | TB | 220 | 1 | 15.5 | -12.3 | 5.6 | 42.7 | 23.3 | 11.2 | -3.7 | -6.7 | 2.2 | 27.3 | -13.1 | 6.9
CBT | MAY | 220 | 1 | -156.1 | 30.4 | 20.9 | -29.5 | 145.1 | 18.6 | -443.8 | 23.5 | 58.4 | -154.9 | 63.7 | 21.1
CBT | MAY | 220 | 2 | 19.7 | -12.7 | 3.1 | -105.8 | 37.4 | 14.1 | -59.2 | 32.3 | 8.9 | -50 | 5.4 | 6.3
CBT | INC | 220 | 1 | 78.4 | -9.5 | 10.4 | 17.4 | -124.3 | 15.8 | 90.2 | -118.3 | 19.6 | -80.9 | -121.3 | 18.4
LOU | ORL | 220 | 1 | - | - | - | - | - | - | 120.1 | -7.1 | 27.7 | -215.6 | -7.4 | 42.1
MAY | TH | 220 | 1 | -317.7 | 96.5 | 102.2 | -358.8 | 74.1 | 104.4 | -186.9 | 12.4 | 57.6 | -104.7 | -4.3 | 29.9
MAY | SH | 220 | 1 | 19.4 | -65.8 | 25.5 | -57.8 | 19 | 17.2 | -106.7 | -3.2 | 39.7 | -95.8 | 18 | 27.5
MP | PRO | 220 | 1 | 25.9 | -12.3 | 5.3 | 78 | 0.2 | 12.8 | -11.2 | 1 | 2.1 | 30.1 | -7.2 | 5.1
NW | PB | 220 | 1 | -24.3 | 12.9 | 8.3 | -80 | 34.5 | 26.2 | -0.4 | -30.6 | 9.2 | 79.2 | -16.8 | 24.4
OST | TYN | 220 | 1 | 74.4 | -68.6 | 23.3 | -34.5 | -32.7 | 9.3 | -238.4 | 35.2 | 55.5 | -178.5 | -79.5 | 38.1
PB | PB | 220 | 1 | -45.9 | -2.5 | 10.2 | -8.2 | 13.1 | 3.4 | -35.8 | 1.7 | 8 | 83 | 25.1 | 19.3
PB | SHL | 220 | 1 | 21.7 | -9.3 | 4 | -71.8 | 51.6 | 14.9 | 35.4 | -6.2 | 6.1 | -3.8 | -11.8 | 2.1
PB | CKM | 220 | 1 | 89.7 | -37 | 36.4 | 97.8 | -51.9 | 41.5 | -62.3 | -46.5 | 29.1 | -104.6 | -54.5 | 44.2
PB | INC | 220 | 1 | -84.3 | 20.6 | 32.5 | -147.8 | 39.6 | 57.3 | -25.6 | 43.9 | 19 | -16.7 | 26.6 | 11.8
PB | INC | 220 | 2 | -118.1 | 18.1 | 34 | -206 | 38 | 59.7 | -40.7 | 54.7 | 19.4 | -27.4 | 31.8 | 12
PRO | TB | 220 | 1 | -32.4 | -2.3 | 6.9 | -89.8 | 6 | 19.3 | 7.9 | -9.8 | 2.7 | -57.1 | 2 | 12.2
SHL | SHL | 220 | 1 | - | - | - | -163 | -20.6 | 8.8 | - | - | - | -163 | -57.9 | 9.3
TB | KPG | 220 | 2 | -16.9 | 10.2 | 5.6 | -47.3 | -28.4 | 12.6 | 4.2 | 4.4 | 1.7 | -29.9 | 11.5 | 7.3
WOO | ORL | 220 | 1 | - | - | - | - | - | - | -129.1 | 8.4 | 29.8 | 155.2 | 75.2 | 33.6
ORL | ORL | 220 | 1 | - | - | - | - | - | - | -10.2 | 0.5 | 1.7 | -62.8 | 60.2 | 14.7
ORL | ORL | 220 | 1 | - | - | - | - | - | - | -10.2 | 0.5 | 1.7 | -62.8 | 7.9 | 11.1
AA | DRU | 110 | 1 | 9.9 | -14.8 | 18 | 31.2 | -8.8 | 26.8 | 12.7 | -9.8 | 16.2 | 44.3 | -12.2 | 38
ENN (I)
AA |  | 110 | 1 | 6.2 | -19.3 | 20.5 | 17.4 | -7.7 | 15.7 | 7.4 | -15 | 16.9 | 31 | -12.2 | 27.6
LIM (I)
AA |  | 110 | 1 | -1.2 | 15.5 | 8.7 | 7.8 | 13.5 | 7.5 | 29.6 | 2.7 | 16.7 | -8.3 | 24.9 | 12.6
AA | AA | 110 | 1 | - | - | - | 0 | -33.1 | 26.9 | - | - | - | 0 | -33.1 | 26.9
AD | WHI | 110 | 1 | 25.5 | -14.3 | 29.5 | 57.4 | 5.1 | 47.6 | 23.5 | -0.5 | 23.8 | 69.3 | 4 | 57.4
ARI | ARI T | 110 | 1 | -0.6 | 0.3 | 0.7 | -0.8 | -2.2 | 1.9 | 3.8 | -6.4 | 7.1 | -1.2 | -6.7 | 5.6
AGL | DYN | 110 | 1 | 0 | -0.3 | 0.3 | -17.8 | 6.4 | 15.3 | -17.8 | 1 | 16.9 | -17.8 | 0.9 | 14.5
ENN (I)
AGL |  | 110 | 1 | -0.8 | -8.9 | 9 | -21.4 | 9.3 | 19.3 | -6.5 | 6.2 | 9.1 | -9.2 | 6.9 | 9.5
AGL | SH | 110 | 1 | 0.8 | 9.2 | 8.9 | 39.2 | -15.7 | 35.5 | 24.3 | -7.1 | 24.3 | 27 | -7.7 | 23.6
AHA | KLN | 110 | 1 | -0.9 | 0.2 | 1.3 | -5 | -0.4 | 7.4 | -1.2 | 0.3 | 1.9 | -5.3 | -0.4 | 7.8
ADM | GCA | 110 | 1 | - | - | - | -2 | 1.1 | 1.7 | 8.2 | 2.2 | 6 | 9.6 | 3 | 7.2
ADM | INC | 110 | 1 | -32.1 | -7 | 31.9 | -14.5 | -8.1 | 12.4 | -19.7 | -6.9 | 20.3 | -26.5 | -10.2 | 21.2
ANR | DOO | 110 | 1 | -14 | -6.9 | 34.7 | -14 | -6.9 | 34.7 | -14 | -6.9 | 34.7 | -14 | -6.9 | 34.7
ARK | BEG | 110 | 1 | 13.2 | 4.9 | 14.2 | 34.6 | 1 | 28.4 | 37.9 | 1.5 | 38.3 | 62.1 | -6.8 | 51.2
ARK | BOG | 110 | 1 | -7.9 | -0.7 | 4.4 | -17.7 | 3.1 | 8.6 | -27.4 | 7.8 | 16 | -41.4 | 11.5 | 20.5
ARK | PHY | 110 | 1 | - | - | - | - | - | - | 1.2 | 0.3 | 0.7 | 1.2 | 0.3 | 0.6
ARK | PHY | 110 | 2 | - | - | - | - | - | - | 1.1 | 0.3 | 0.6 | 1.1 | 0.3 | 0.5
ATE | DRO | 110 | 1 | 0 | -7.7 | 6.4 | -8.5 | -0.7 | 6.1 | -8.5 | 4.2 | 7.9 | -8.5 | 3.6 | 6.6
ATE | ATE | 110 | 1 | - | - | - | -2.3 | 1.1 | 1.2 | -2.3 | 2.2 | 1.8 | -2.3 | 2.2 | 1.5
ATE | KNR | 110 | 1 | 0 | 7.7 | 4.3 | 31.3 | -25.9 | 19.3 | 21.1 | -18.9 | 15.9 | 31.3 | -25.5 | 19.2
ATH | LA | 110 | 1 | 19.4 | 4.2 | 20 | 26.3 | 4.5 | 22 | 3.8 | 10.5 | 11.3 | 26.3 | -4.8 | 22.1
ATH | SH | 110 | 1 | -38.4 | 37.7 | 30.3 | -108.8 | 49.9 | 63 | -30.3 | 25.5 | 22.3 | -113.5 | 20.9 | 60.7
BKE | AUG | 110 | 1 | - | - | - | 56.7 | 1.5 | 27 | 26.4 | 24.8 | 20.3 | -50 | 15 | 24.9
BKE | KPG | 110 | 1 | - | - | - | -56.7 | -1.5 | 27 | -26.4 | -24.8 | 20.3 | 50 | -15 | 24.9
AUG | CFM | 110 | 1 | 25.4 | 14.1 | 30.3 | 25.4 | 14.1 | 30.3 | 25.4 | 14.6 | 30.5 | 25.4 | 14.2 | 30.4
AUG | MTN | 110 | 1 | -16 | -4.3 | 9.3 | 5.8 | 7.1 | 4.4 | -24.5 | -3.2 | 13.9 | 61 | 0.8 | 29
AUG | SK | 110 | 3 | 0 | -0.7 | 0.6 | 0 | -17 | 14.2 | 0 | -0.6 | 0.5 | -80.9 | -7.2 | 67.7
AUG | SK | 110 | 4 | 0 | -0.7 | 0.6 | 0 | -17 | 14.2 | 0 | -0.6 | 0.5 | -80.9 | -7.2 | 67.7
AUG | CFM | 110 | 2 | 25.4 | 14.1 | 30.3 | 25.4 | 14.1 | 30.3 | 25.4 | 14.6 | 30.5 | 25.4 | 14.2 | 30.3
ARV | COS | 110 | 1 | -11.4 | -6 | 12.4 | -56 | 22.2 | 49 | -30 | 6.9 | 22.5 | -55.3 | 10 | 41
ARV | GWE | 110 | 1 | 24.5 | -9 | 14.7 | -22 | 1.6 | 10.5 | -12.2 | 15.4 | 11.1 | 31.7 | 0.5 | 15.1
ARV | NAV | 110 | 1 | -11.3 | 21 | 13.4 | 8.7 | 9.3 | 6.1 | 30.3 | 0.2 | 17 | 2.8 | 7.1 | 3.6
ARV | SKL | 110 | 1 | -1 | -3.2 | 2.5 | 38.8 | -18.4 | 31.3 | 6.6 | -12.5 | 10.3 | 11.6 | -9.7 | 11
ARV | SKL | 110 | 2 | -0.8 | -2.8 | 1.6 | 30.6 | -14.8 | 16.2 | 5.2 | -10.1 | 6.4 | 9.1 | -7.9 | 5.8
ART | FIN (I) | 110 | 1 | -2.1 | 0.4 | 1.8 | -35.4 | -3.1 | 27.1 | -10.9 | -0.2 | 9.1 | -37.4 | -3.6 | 28.7
ART | MCD | 110 | 1 | -0.1 | -1.1 | 0.9 | 20.6 | 2.2 | 15.8 | 7.8 | -0.9 | 6.6 | 21.8 | 2.6 | 16.7
BVK | GRO | 110 | 1 | 0 | -27.3 | 14 | -54.6 | 20.2 | 26.5 | -54.3 | 25.1 | 30.7 | -54.4 | 26.2 | 27.4
BVK | BVK | 110 | 1 | - | - | - | - | - | - | 0 | 35 | 16 | 0 | 15.1 | 6.5
ATY | CLW | 110 | 1 | -32.1 | 13.8 | 35.3 | -61 | 9 | 51 | -18.3 | 4.3 | 19 | -36.8 | 11.8 | 31.9
ATY | CNB | 110 | 1 | - | - | - | - | - | - | 12.3 | -5.9 | 7.7 | 16.2 | -19.9 | 12.2
BWR | CRA | 110 | 1 | 0 | -14.4 | 21.1 | 12.6 | -9.1 | 22.8 | 12.6 | -7.8 | 21.8 | 12.6 | 3.5 | 19.2
ENN (I)
BOL |  | 110 | 1 | 19.6 | -0.1 | 11 | 76 | -11.8 | 36.6 | 11.7 | 4.1 | 7 | 46 | -1.5 | 21.9
BOL | TBK T | 110 | 1 | -19.6 | 2.8 | 11.1 | -41.3 | -6.4 | 19.9 | 3.5 | -5.7 | 3.8 | -4.3 | -10.1 | 5.2
BAL | DEE | 110 | 1 | - | - | - | - | - | - | -50.9 | 0 | 28.6 | 64 | 7.8 | 30.7
BAL | CDU | 110 | 1 | -15.1 | 23.2 | 15.5 | -92.3 | -10.1 | 44.4 | 46.4 | 0.1 | 26.1 | -81.4 | -10.2 | 39.3
BLI | DMY | 110 | 1 | -4.3 | 4.5 | 9.1 | 5.4 | -7.8 | 13.9 | 6.7 | -0.3 | 9.9 | 4.6 | -2.6 | 7.8
BEG | CKM | 110 | 1 | 10.2 | 5.9 | 8.6 | 18.9 | 0.4 | 11.9 | 33.6 | 1.7 | 24.7 | 45.4 | -9.5 | 29.2
CDL | BYH | 110 | 1 | 0 | 14.3 | 7.3 | 49.3 | -35.3 | 27.6 | 20 | 1 | 10.3 | 49.3 | -38.4 | 28.4
BLK | BLK T | 110 | 1 | -5.9 | 0.1 | 4.4 | -26.5 | -6.3 | 17.1 | -6.7 | 0.2 | 5 | -28 | -6.1 | 18.1
BLU | CDU | 110 | 1 | - | - | - | -9 | 3.9 | 7.6 | 25.4 | -0.7 | 19.6 | -10.1 | 3.7 | 8.3
BLU | MUL | 110 | 1 | - | - | - | 9 | -3.9 | 8 | -25.4 | 0.7 | 24.2 | 10.1 | -3.7 | 8.7
BIN | CF | 110 | 1 | -8.7 | 6.1 | 10.7 | 3 | -6.1 | 5.6 | -2.5 | 6.9 | 7.5 | -14 | 2.1 | 11.7
BIN | TIV | 110 | 1 | 4.3 | -5.4 | 5.1 | 10.5 | -1.9 | 6.7 | 15.6 | -14.1 | 15.5 | 36.6 | -9.4 | 23.8
BDA | MON | 110 | 1 | -15.4 | 10 | 18.6 | -4.8 | 0.5 | 4 | 2.6 | -1.5 | 3 | 17.8 | -15.6 | 19.5
NEW (I)
BDA |  | 110 | 1 | 10.2 | -10.9 | 12.2 | -0.5 | -1.4 | 1.2 | -7.8 | 0.7 | 6.4 | -23 | 14.8 | 22.4
BDN | CUL | 110 | 1 | -39.8 | 25.2 | 24 | -36.4 | 3.5 | 16.8 | -0.8 | -7.8 | 4 | -64.7 | 27.7 | 32.4
BDN | DOO | 110 | 1 | 31.1 | -27.6 | 23.4 | 15.2 | -8.7 | 8.3 | -8.9 | 5.2 | 5.8 | 42.7 | -33.2 | 25.8
BAH | CLG | 110 | 1 | - | - | - | - | - | - | 7.2 | 7.3 | 5.3 | 7.2 | 7 | 5.3
BAH | SBH | 110 | 1 | - | - | - | - | - | - | -26.2 | -13.6 | 15.4 | -26.3 | -13.4 | 15.3
BRY | RAF | 110 | 1 | -13 | -2.8 | 21 | -24.2 | -6.4 | 27.2 | -18 | -4.2 | 29.3 | -25.6 | -6.8 | 28.7
BRY | RAF | 110 | 2 | -6 | -1.2 | 6.2 | -11.1 | -2.7 | 9.5 | -8.3 | -1.8 | 8.6 | -11.8 | -2.9 | 10
BK | CBR | 110 | 1 | -9 | 4 | 5 | 15.9 | -7.2 | 7.9 | 25.6 | -12.4 | 14.6 | 33.3 | -17.5 | 17
BK | MOY | 110 | 1 | 7.8 | 2.2 | 5.9 | 32 | -11.4 | 24.8 | 26.9 | -4.3 | 19.9 | 49.6 | -14.9 | 37.8
BGD | INC | 110 | 1 | -22.3 | -7.3 | 16.8 | -22.3 | -7.3 | 16.8 | -26.6 | -8.7 | 20 | -26.6 | -8.7 | 20
BGD | INC | 110 | 2 | -22.3 | -7.3 | 16.8 | -22.3 | -7.3 | 16.8 | -26.6 | -8.7 | 20 | -26.6 | -8.7 | 20
BLA | RE | 110 | 1 | -11.2 | 2.6 | 9.6 | -46.6 | -6.6 | 39.5 | -15.5 | 3.5 | 13.4 | -49.2 | -7.3 | 41.8
BGT | KKY | 110 | 1 | - | - | - | - | - | - | -13.7 | 3.3 | 7.9 | -43.5 | 5.2 | 20.8
BGT | CNB | 110 | 1 | - | - | - | - | - | - | 6 | -5.2 | 4.5 | 15.7 | -14.4 | 10.1
BAN | BRI | 110 | 1 | 2 | 0.4 | 4.5 | 2 | 0.4 | 4.5 | 2 | 0.4 | 4.5 | 2 | 0.4 | 4.5
BAN | DMY | 110 | 1 | 2.3 | -22 | 22.3 | -22.7 | 5.7 | 19.4 | -13.9 | -2.3 | 14.2 | -11.8 | -3.1 | 10.1
BAN | RAF | 110 | 1 | -20 | 18.8 | 27.8 | -30.7 | -2.1 | 25.5 | -7.1 | -1.6 | 7.3 | -44.5 | 6.6 | 37.1
BAN | BAN | 110 | 1 | - | - | - | 0 | -16.5 | 13.4 | - | - | - | 0 | -16.5 | 13.4
BAN | BRI | 110 | 2 | 2 | 0.4 | 4.5 | 2 | 0.4 | 4.5 | 2 | 0.5 | 4.5 | 2 | 0.4 | 4.5
CLG | CDU | 110 | 1 | -76 | -28.1 | 43.3 | -76.7 | -27.5 | 37.2 | -74.7 | -24.7 | 42.1 | -74.7 | -24 | 35.8
BAR | BAR T | 110 | 1 | -8.2 | 2.2 | 6.2 | -22 | -9 | 14.9 | 0.5 | 2.5 | 1.9 | -23.7 | -4.5 | 15.2
BLC | DRN | 110 | 1 | 29.5 | 8.1 | 13.4 | 29.5 | 7.8 | 13.4 | 54.3 | 19.4 | 25.3 | 54.3 | 18.5 | 25.1
BLC | DRN | 110 | 2 | 29.5 | 8.1 | 13.4 | 29.5 | 7.8 | 13.4 | 54.3 | 19.4 | 25.3 | 54.3 | 18.5 | 25.1
BLC | DTN | 110 | 2 | -4.3 | -8.9 | 7.1 | 4.1 | -6.3 | 5.3 | -4.5 | -11.4 | 8.8 | 9.1 | -6.7 | 7.9
BLC | GRA | 110 | 1 | -1.2 | -11.5 | 8.2 | 29.1 | 0 | 20.8 | -0.8 | -14.9 | 10.6 | 37.5 | -0.7 | 26.8
BLC | KLM | 110 | 1 | -1 | -9 | 6.5 | 17.3 | -3 | 12.6 | -1.9 | -12.9 | 9.3 | 25.4 | -4 | 18.3
BUT | CUL | 110 | 1 | -3.5 | -4.3 | 3.1 | -39.9 | -1.4 | 20.8 | -20.8 | 2.5 | 11.8 | -37.3 | -8.6 | 19.9
BUT | KTN | 110 | 1 | -5.7 | 4.7 | 3.7 | -1.3 | -8.8 | 4.1 | 8.6 | -2.1 | 4.4 | -6.2 | -2.6 | 3.1
DEE | DRY | 110 | 1 | - | - | - | - | - | - | -51.1 | -0.5 | 28.7 | 63.7 | 6.9 | 30.5
KNG | TRI | 110 | 1 | 0 | 1.4 | 1.2 | 30.1 | -22.9 | 30.5 | 26.3 | -19.3 | 26.3 | 30 | -26.2 | 32.1
BDM | MID | 110 | 1 | - | - | - | - | - | - | 10.6 | -2.4 | 11 | 38.4 | 1.4 | 31.7
BDM | WHI | 110 | 1 | - | - | - | - | - | - | -10.6 | 2.4 | 11 | -38.4 | -1.4 | 31.7
BOG | TUL | 110 | 1 | - | - | - | -26.4 | 3 | 12.6 | -29.4 | 7.8 | 17.1 | -50.9 | 9.9 | 24.7
BGH | CLA | 110 | 1 | 0 | 0.7 | 0.4 | 42.6 | -25.2 | 23.6 | 56.6 | -26.4 | 35.1 | 48.8 | -22.2 | 25.6
AGY | TIV | 110 | 1 | -3.4 | -0.4 | 3.2 | -9.2 | -5.7 | 8.8 | -3.2 | -2 | 3.6 | -10.1 | -6.7 | 9.9
CAB | PTN | 110 | 1 | -1.6 | 0.4 | 2.1 | -20 | -5 | 17.3 | -7.4 | -0.7 | 9.3 | -21.1 | -5.5 | 18.3
CAB | WOL | 110 | 1 | -2 | -1.6 | 2.1 | 4.6 | -0.2 | 3.5 | 2.5 | -0.9 | 2.2 | 4.9 | -0.1 | 3.7
CFD | KIN | 110 | 1 | - | - | - | - | - | - | 7.5 | 4.7 | 5 | -21 | 9.2 | 10.9
CFD | MUL | 110 | 1 | - | - | - | - | - | - | -7.5 | -4.7 | 5 | 21 | -9.2 | 10.9
CLA | CKN | 110 | 1 | 26.9 | -23.5 | 20.1 | 46.3 | 2.8 | 24.4 | 28.1 | -11.2 | 17 | 71 | 3.6 | 37.4
CLA | DMY | 110 | 1 | 3.5 | 5.7 | 3.8 | 13.3 | 0.8 | 6.3 | 3.6 | -1.5 | 2.2 | 6.5 | -2.4 | 3.3
CLA | MAC | 110 | 1 | -1.1 | 15.9 | 9.9 | 22.8 | -1.3 | 12 | 5.7 | -2.3 | 3.8 | 6.4 | 1.7 | 3.5
CKN | KER | 110 | 1 | 26.7 | -22.9 | 19.8 | 45.9 | 2.6 | 21.9 | 27.9 | -10.6 | 16.8 | 70.2 | 0.8 | 33.4
CRO | IA | 110 | 1 | 3.1 | -24.1 | 12.4 | -36.8 | 9.4 | 17.5 | -25.8 | 5.7 | 13.5 | -22.8 | -1.7 | 10.5
CRO | KBY | 110 | 1 | -6.4 | 24 | 14 | 25.9 | -9.7 | 13.8 | 21.2 | -5.6 | 12.3 | 11.2 | 1.6 | 5.7
CDY | GRV | 110 | 1 | 0 | 9.6 | 10.5 | -24.5 | -6.2 | 27.7 | -24.5 | 6.9 | 27.9 | -24.5 | 2.7 | 27.1
CDY | SRA | 110 | 1 | 5.8 | -18.2 | 10.7 | 8 | 0 | 3.8 | 5.8 | -2.5 | 3.6 | 25.3 | -9.2 | 12.8
CDY | ARI T | 110 | 1 | -5.9 | 9.6 | 6.3 | 35.1 | -2.4 | 16.8 | 30.8 | -4.3 | 17.4 | 17.9 | 6.3 | 9
CSH | CLN | 110 | 1 | 26 | -1 | 14.6 | 81.4 | -2.4 | 38.8 | 18.5 | -8.6 | 11.5 | 65.3 | 1.9 | 31.1
CSH | DLT | 110 | 1 | 17.7 | -9.7 | 20.4 | 31 | -3.8 | 25.8 | -5.1 | -3.1 | 6.1 | 24.3 | -5 | 20.5
ENN (I)
CSH |  | 110 | 1 | -9.6 | 8.9 | 7.4 | -27.8 | 18.8 | 16 | 1.6 | 0.6 | 0.9 | -31.3 | 16.4 | 16.8
CSH | GAL | 110 | 1 | 9.2 | -21 | 23.1 | 14.1 | 10.7 | 14.6 | -2.3 | 2.4 | 3.2 | 16.2 | 5.6 | 13.9
CSH | GAL | 110 | 2 | 11.2 | -25.5 | 28.1 | 17.2 | 13.1 | 17.9 | -2.8 | 3.1 | 4 | 19.7 | 6.9 | 17
CSH | GAL | 110 | 3 | 11.2 | -25.5 | 28.1 | 17.2 | 13.1 | 17.9 | -2.8 | 3.1 | 4 | 19.7 | 6.9 | 17
CSH | SAL | 110 | 1 | 8.6 | -18.5 | 21 | 9.2 | 3.6 | 10.1 | -0.7 | -3.1 | 3.3 | 11.1 | 0.2 | 11.4
CSH | SHN | 110 | 1 | -3.2 | 19.8 | 19.1 | 29.3 | 1.1 | 23.9 | 22.8 | -8.8 | 23.3 | 10.1 | 7 | 10
CSH | CSH | 110 | 1 | - | - | - | 0 | -91.9 | 74.7 | - | - | - | 0 | -45.4 | 36.9
CLH | TRI | 110 | 1 | 1 | 0.2 | 1.1 | -3.2 | -6.7 | 6.2 | 13 | 0.3 | 13.1 | 5 | -6.3 | 6.7
CLH | TRL | 110 | 1 | -1 | -0.2 | 1 | 18.6 | -4.9 | 15.6 | -1.7 | -0.9 | 1.8 | 10.4 | 5.4 | 9.5
CBR | CLN | 110 | 1 | -12.8 | 9.2 | 15.9 | -10.3 | -3.7 | 9.1 | 14.2 | 0 | 8 | -4.6 | -3.7 | 2.8
CBR | CBG | 110 | 1 | 6 | -6.9 | 9.2 | 18.8 | -2.3 | 15.6 | 8.3 | -5.1 | 9.8 | 19.8 | -2 | 16.5
CBR | DLT | 110 | 1 | -9.8 | 4.7 | 11 | -13.9 | -2 | 11.6 | 2.8 | 0.6 | 2.9 | -5.8 | -5.7 | 6.7
CBR | CBR | 110 | 1 | - | - | - | - | - | - | - | - | - | 0 | -33.1 | 26.9
CCN | CUS | 110 | 1 | - | - | - | - | - | - | 0 | -0.6 | 0.4 | 22.5 | -0.7 | 16.1
CD | MAC | 110 | 1 | 10.8 | -25.3 | 15.5 | -22.1 | 0.7 | 10.5 | -9 | -1.1 | 5.1 | 0.9 | -4.8 | 2.3
CD | KLP | 110 | 1 | - | - | - | - | - | - | 17 | -0.5 | 9.6 | 7.1 | 3.3 | 3.7
CPK | TNY | 110 | 1 | 2 | -7.5 | 7.7 | 10 | -7.1 | 12.3 | 2.8 | -7.3 | 7.8 | 10.6 | -7 | 12.7
CF | CL | 110 | 1 | 0 | -0.2 | 0.4 | -19.9 | 3.9 | 29.8 | -19.9 | 7.4 | 31.2 | -19.9 | 6.2 | 30.6
CF | COR | 110 | 1 | 1.2 | 19 | 10.7 | 52.8 | -4.1 | 25.3 | 33.5 | -6.5 | 19.2 | 36.7 | 0.6 | 17.5
CF | SRA | 110 | 1 | -12.7 | 14.3 | 9.7 | 7.9 | -1.9 | 3.5 | 8.9 | -8.8 | 6.4 | -22.3 | 6.8 | 9.9
CF | CF | 110 | 1 | - | - | - | 0 | -16.5 | 13.5 | - | - | - | 0 | -16.5 | 13.5
CF | CLO | 110 | 2 | 5.4 | -19.5 | 11.4 | -8.8 | 0.4 | 4.2 | 1.9 | -13.6 | 7.7 | 21.2 | -11.8 | 11.6
CAH | DOO | 110 | 1 | -10.6 | 33.5 | 19.8 | 27.3 | 3.5 | 13.1 | 31.8 | 0.6 | 17.9 | 1.6 | 30.5 | 14.5
CAH | KHL | 110 | 1 | 16.3 | -18.2 | 13.7 | 17.7 | 13.4 | 10.6 | -7.2 | -1.3 | 4.1 | 21.6 | 0.4 | 10.3
CAH | TIP | 110 | 1 | 10.4 | -31.8 | 18.8 | -31 | 21.2 | 17.9 | -14.5 | -3.2 | 8.4 | -5.6 | 5.1 | 3.6
CAH | BAR T | 110 | 1 | -21.2 | 16.1 | 25.3 | -41.4 | 24.4 | 39 | -18.4 | 3.7 | 17.8 | -46.5 | 25.4 | 43.1
CAH | CAH | 110 | 1 | - | - | - | 0 | -67.6 | 54.9 | - | - | - | 0 | -66.9 | 54.4
CKM | CHE | 110 | 1 | 3 | -4.5 | 5.2 | 16.3 | 2 | 13.4 | 4.2 | -5 | 6.3 | 17.2 | 2.3 | 14.1
CKM | POT | 110 | 1 | 4.4 | -4.3 | 5.2 | 17.2 | -3.5 | 14.7 | 6.1 | -3.5 | 5.9 | 18.2 | -3.3 | 15.5
CKM | CPK | 110 | 1 | 5.4 | -10.3 | 8.5 | 21.8 | -8.9 | 17.2 | 7.5 | -10.1 | 9.3 | 23.1 | -8.7 | 18
NEW (I)
BRA |  | 110 | 1 | 7 | 7.8 | 7.7 | 21.1 | -11.5 | 15.1 | 35.9 | -3.3 | 26.5 | 52.2 | -12.8 | 33.8
BRA | PLS | 110 | 1 | -7 | -7.8 | 10.6 | -21.1 | 11.5 | 19.8 | -35.9 | 3.3 | 36.4 | -52.2 | 12.8 | 44.4
COO | BCT | 110 | 1 | 2.7 | 2 | 2.6 | 2.7 | 2.1 | 2.6 | 2.7 | 2 | 2.6 | 2.7 | 2.1 | 2.6
COO | CKM | 110 | 2 | -2.7 | -2 | 2.6 | -2.7 | -2.1 | 2.6 | -2.7 | -2 | 2.6 | -2.7 | -2.1 | 2.6
CLU | KUD | 110 | 1 | - | - | - | - | - | - | 10.6 | 2.9 | 5.9 | 10.6 | 2.5 | 4.9
CLU | CBT | 110 | 1 | - | - | - | - | - | - | -51.5 | -16.9 | 29 | -51.4 | -16.4 | 24.2
CLN | LA | 110 | 1 | 7.9 | 10.8 | 13.5 | 44 | -9.2 | 37.2 | 26.9 | -7.4 | 28.2 | 32.5 | -3.8 | 27
SCR | KNY | 110 | 1 | -5.5 | 1.3 | 4.2 | -16.4 | -3.4 | 10.6 | -7.6 | 1.6 | 5.7 | -17.4 | -2.4 | 11.1
CRA | LWD | 110 | 1 | -20 | 11.9 | 13.1 | -61.4 | 8.1 | 29.5 | -18.4 | 10.3 | 11.8 | -73.6 | 12.3 | 35.5
CRA | TUL | 110 | 1 | - | - | - | 26.5 | -3.6 | 12.7 | 29.6 | -8 | 17.2 | 51.3 | -9 | 24.8
CRA | WEX | 110 | 1 | 2.2 | 3.4 | 4.1 | 17.1 | -8.3 | 16.8 | -8.2 | 3.1 | 8.9 | 2.7 | 3.9 | 4.2
COS | FLA | 110 | 1 | -11.7 | 3.4 | 12.3 | -26.7 | 5.3 | 22.5 | -1.9 | -1.5 | 2.5 | -35 | 2 | 28.9
COS | FLA | 110 | 2 | -12 | 3.6 | 12.6 | -27.3 | 5.5 | 23 | -1.9 | -1.6 | 2.5 | -35.8 | 2.2 | 29.7
COS | ARI T | 110 | 1 | 6.5 | -11.3 | 7.3 | -34.1 | 4.5 | 16.4 | -34.3 | 10.7 | 20.2 | -16.7 | -0.5 | 8
COL (I)
| FIN (I) | 110 | 1 | 6 | -0.3 | 5.7 | 5.2 | -0.6 | 4.2 | 1.1 | -2.8 | 2.9 | 4 | -3.4 | 4.3
COL (I)
| CDU | 110 | 1 | -17.3 | -1.2 | 12.1 | -22 | -1.6 | 15.4 | -16.8 | 0.6 | 11.8 | -21.8 | 1.1 | 15.3
CHA | GLE | 110 | 1 | 3.6 | 0.1 | 3.6 | 10 | 5.2 | 9.3 | -2.8 | 1 | 3 | 11 | 1.9 | 9.2
CHA | KLN | 110 | 1 | 14.2 | -24.8 | 21 | 8.1 | -16.7 | 11.7 | 16.6 | -4.8 | 12.7 | 25.5 | -16.4 | 19.1
CHA | MAL | 110 | 1 | -22.5 | 27.4 | 19.9 | -17.9 | 0 | 8.5 | -2 | 2.3 | 1.7 | -37.5 | 8.2 | 18.3
CLW | KLS | 110 | 1 | -24.5 | 9.2 | 26.4 | -59.2 | -14.9 | 50.4 | 0.8 | -11.5 | 11.6 | -47.3 | -8.3 | 39.7
CLW | KLS | 110 | 2 | -24.7 | 9 | 26.5 | -59.3 | -15.5 | 50.6 | 1 | -11.5 | 11.7 | -47.4 | -8.8 | 39.9
CLW | STR T | 110 | 1 | 3.6 | -1.4 | 5.8 | -5.3 | 17.8 | 27.4 | -28.1 | 22.2 | 52.6 | -7.9 | 1.9 | 12
COW | CVW | 110 | 1 | 8.7 | -9.2 | 12.8 | 22.1 | -0.8 | 18.3 | 10 | -2.8 | 10.5 | 29.7 | 0.4 | 24.5
COW | OLD | 110 | 1 | 0.3 | 0 | 1 | 0.3 | 0 | 1 | 0.3 | 0 | 1 | 0.3 | 0 | 1
COW | RAF | 110 | 1 | -10.3 | 0.7 | 10.5 | -24.5 | -2.1 | 20.3 | -14.5 | -0.1 | 14.6 | -27 | -5.1 | 22.7
COW | WHI | 110 | 1 | -4.5 | 8.4 | 9.7 | -15.3 | 1.5 | 12.7 | -3.9 | 2.7 | 4.7 | -21.3 | 3.1 | 17.8
CUN | GLR | 110 | 1 | -0.5 | -6.9 | 3.9 | -27.1 | 8.7 | 13.6 | -15.3 | -0.2 | 8.6 | -34.9 | 13.2 | 17.8
CUN | SLI | 110 | 1 | 0.5 | 14.3 | 8 | 37.2 | -7.9 | 18.2 | 25.5 | 1.2 | 14.4 | 45.1 | -7.4 | 21.9
CUS | MLC | 110 | 1 | 5.5 | -0.9 | 4.1 | 3 | 38.1 | 24 | 0.7 | 0.3 | 0.6 | 20.3 | -17.6 | 16.9
NEW (I)
CUS |  | 110 | 1 | 0.8 | 6.3 | 4.7 | 12.6 | 32.3 | 22.8 | 23.1 | -0.5 | 17.3 | 36.2 | 4.4 | 24
CUS | PLS | 110 | 1 | -6.3 | -5.4 | 6.1 | -15.7 | 29.7 | 21.1 | -23.9 | 0.8 | 17.6 | -34.1 | 13.1 | 23
CVW | KRA | 110 | 1 | -1.9 | -9 | 9.3 | -11.5 | -8 | 11.6 | -13.6 | -6.6 | 15.3 | -13.6 | -9.9 | 13.9
CGL | GAE | 110 | 1 | 0 | -2.9 | 3.2 | -8.9 | 8.4 | 13.4 | -8.9 | 5.8 | 11.6 | -8.9 | 8.4 | 13.4
CGL | CKN | 110 | 1 | 0 | 2.9 | 1.6 | 33.1 | -26 | 22.2 | 33.1 | -18.9 | 21.4 | 33.1 | -22.7 | 21.1
COR | GWE | 110 | 1 | 1.3 | 19.4 | 10.9 | 53.5 | -5.3 | 25.6 | 39 | -2.3 | 21.9 | 0.3 | -3.5 | 1.7
ENN (N)
COR |  | 110 | 1 | -0.3 | 1.6 | 1.7 | -1.7 | -1.5 | 1.9 | -6 | -4.4 | 7.5 | 35.9 | 4 | 29.8
CDK | LWD | 110 | 1 | 0 | -5.4 | 5.9 | 12.5 | -9 | 16.9 | 12.2 | -11.6 | 18.5 | 12.5 | 10 | 17.5
CUL | RTO | 110 | 1 | - | - | - | - | - | - | -18.3 | 2.9 | 10.4 | 2 | 1.8 | 1.3
CUL | WAT | 110 | 1 | 1.4 | 3.7 | 2.2 | 48.7 | -7.8 | 24.7 | 29.7 | -7.9 | 17.3 | 43.2 | 4.2 | 21.7
CTY | FTT | 110 | 1 | 19.1 | -5.9 | 16.1 | 87.9 | 16.1 | 67.7 | 26.6 | -6.2 | 22 | 92.9 | 18.3 | 71.7
CTY | INC | 110 | 1 | -26.2 | 3.4 | 25.7 | -100.9 | -20.3 | 83.7 | -36.5 | 2.6 | 35.5 | -106.6 | -22.8 | 88.6
CDU | GAN | 110 | 1 | - | - | - | - | - | - | 0 | -0.4 | 0.2 | 0 | -0.4 | 0.2
CDU | RYB | 110 | 1 | 8.1 | 22.5 | 13.4 | -17.7 | 34.8 | 17.8 | 3.6 | 23.6 | 13.4 | 23.1 | 31.7 | 17.9
KNY | UGL | 110 | 1 | 0 | -5.3 | 2.7 | -52 | 39.7 | 29.7 | -50.5 | 40.3 | 33.1 | -52 | 26.2 | 26.5
KNY | GAL | 110 | 1 | 0 | 44.7 | 45.1 | 52 | -39.7 | 54 | 50.5 | -40.3 | 36.1 | 52 | -26.2 | 31.5
KNY | KLH | 110 | 1 | 0 | -14.2 | 7.5 | -10 | -0.1 | 5.3 | 0 | -11.3 | 6 | -10.1 | -11.9 | 8.2
KNY | SAL | 110 | 1 | -5.5 | 20.8 | 11 | 20.8 | 9.1 | 10.3 | -7.6 | 17.7 | 9.9 | 19.9 | 13.3 | 10.9
KNY | BUF | 110 | 1 | - | - | - | -27.3 | -8 | 20.3 | 0 | -0.6 | 0.4 | -27.3 | 0.4 | 19.5
DDK | MLN | 110 | 1 | -5.6 | -4.6 | 7.3 | -39.9 | -16.6 | 35.7 | 1.9 | -2.6 | 3.2 | -28.5 | -16 | 27
DDK | LOU | 110 | 1 | -7.5 | 8.5 | 11.5 | -23.5 | 2.8 | 19.5 | -15 | 6.1 | 16.4 | -38.7 | 3.3 | 32.1
ENN (I)
DRU |  | 110 | 1 | 0.7 | -19.5 | 19.7 | -0.7 | -4.4 | 3.7 | -0.1 | -16.9 | 17 | 10.4 | -9.4 | 11.6
DRU | DRU | 110 | 1 | - | - | - | 0 | -16.5 | 13.4 | - | - | - | 0 | -16.4 | 13.3
DGN | RTO | 110 | 1 | - | - | - | - | - | - | 18.4 | -3.8 | 10.5 | -2 | -3.2 | 1.8
DGN | WHO | 110 | 1 | -6.8 | -5.5 | 4.9 | -63.1 | 6.8 | 30.2 | -31.9 | 3.3 | 18 | -50 | -9.4 | 24.2
DRG | KPG | 110 | 1 | - | - | - | -11.9 | -7.1 | 6.6 | 7.6 | 2.3 | 4.5 | -3.7 | -8.2 | 4.3
DRG | TRL | 110 | 1 | - | - | - | 11.9 | 7.1 | 6.6 | -7.6 | -2.3 | 4.5 | 3.7 | 8.2 | 4.3
DOO | DOO | 110 | 1 | - | - | - | 0 | -16.8 | 13.6 | - | - | - | 0 | -16.2 | 13.2
DRY | GOR | 110 | 1 | -6.1 | -8.9 | 10.9 | 3.2 | -1.2 | 2.8 | -37.3 | -2.2 | 37.7 | -24.1 | -3.8 | 20.2
DRY | LOU | 110 | 1 | 0.9 | -26.8 | 27.1 | 24.2 | -24 | 28.2 | -58.6 | -14.3 | 60.9 | -40.6 | -28.8 | 41.1
DRY | OBE | 110 | 1 | - | - | - | - | - | - | 22.7 | 15.4 | 26.1 | 32.6 | 14.1 | 28.8
DMY | MAC | 110 | 1 | -5.9 | -4.8 | 3.9 | -13 | 0.3 | 6 | -3.4 | 0.9 | 1.8 | -6.5 | 3.4 | 3.4
DMY | CDN | 110 | 1 | 0 | -0.4 | 0.2 | -16.2 | 9 | 8.6 | 0 | -0.4 | 0.2 | -20.3 | 0.3 | 9.4
DMY | DMY | 110 | 1 | - | - | - | 0 | -16.6 | 13.5 | - | - | - | 0 | -16.7 | 13.6
DAL | DAL | 110 | 1 | 0 | 0.4 | 0.4 | -13 | -7.1 | 12 | -1.4 | -1.9 | 2.3 | -14.1 | -8.4 | 13.3
DTN | FIN (I) | 110 | 1 | -17.2 | -6.9 | 13.2 | -13.6 | -4.5 | 10.3 | -19.1 | -11 | 15.8 | -8.3 | -4.7 | 6.9
DTN | KLM | 110 | 1 | 7 | 2.2 | 5.3 | 10.4 | 3.1 | 7.7 | 6.5 | 3 | 5.1 | 9.6 | 2.9 | 7.1
DER | KIN | 110 | 1 | 23.2 | -9.4 | 25.3 | 26.4 | 2.5 | 21.9 | 24.7 | -0.9 | 24.9 | 25.1 | -2.2 | 20.9
DER | TIM | 110 | 1 | - | - | - | - | - | - | -9.8 | -0.6 | 5.5 | -18.4 | -0.2 | 8.8
DER | TSB | 110 | 1 | 2.3 | -2.7 | 3.6 | 8.5 | -1.3 | 7.1 | -14.9 | 1.5 | 15.1 | -6.8 | 2.4 | 5.9
DLT | DLT | 110 | 1 | - | - | - | 0 | -16.8 | 13.6 | - | - | - | 0 | -16.8 | 13.6
DFR | DFR | 110 | 1 | -2.3 | 0.1 | 4.1 | -11.1 | -3.9 | 20.6 | -3.2 | 0.1 | 5.7 | -11.7 | -4.2 | 21.9
DRM | LET | 110 | 1 | 8.2 | 2.1 | 8.5 | 30.2 | -13.9 | 27 | 43.5 | -19.2 | 48 | 84.5 | -19.5 | 70.5
DRM | MEE | 110 | 1 | 0 | -0.2 | 0.2 | -25.4 | 14.9 | 24.3 | -25.4 | 1.8 | 25.7 | -25.4 | 1.7 | 21
DRM | CLO | 110 | 1 | -8.2 | -1.9 | 8.1 | -4.9 | -1 | 4 | -18.1 | 17.4 | 24.4 | -59.1 | 17.8 | 50.2
ENN (I)
| SLC | 110 | 1 | 0 | -34 | 17.4 | -21.6 | -14.1 | 11.7 | -8.1 | -18.2 | 10.2 | -21.6 | -16.4 | 12.3
KHL | THU | 110 | 1 | 16.2 | -17.8 | 13.5 | 28.5 | 0.8 | 13.6 | -7.2 | -0.7 | 4.1 | 32.4 | 0.4 | 15.4
MLC | TSB | 110 | 1 | 5.5 | -0.3 | 4.1 | 27.8 | 8.1 | 18.2 | 25.9 | -3.3 | 19.3 | 45.3 | 4.6 | 28.6
CKG | CBT | 110 | 1 | 0 | -0.9 | 0.5 | -28.6 | -10.1 | 13.6 | -64.7 | -25.8 | 37.3 | -64.6 | -25.2 | 31.1
CKG | CBT | 110 | 2 | - | - | - | -28.6 | -10.1 | 13.6 | -64.7 | -25.8 | 37.3 | -64.6 | -25.2 | 31.1
FAS | FAS | 110 | 1 | -5.5 | -1.9 | 5.6 | -30.7 | -12.2 | 26.9 | -7.7 | -2.8 | 7.8 | -32.4 | -13.5 | 28.6
FAS | CKM | 110 | 1 | -5.6 | -2 | 5.6 | -30.8 | -12.4 | 27 | -7.7 | -2.8 | 7.8 | -32.5 | -13.7 | 28.7
FLA | GIL | 110 | 1 | 11.4 | 2.9 | 17.3 | 11.5 | -10.8 | 23.1 | 11.4 | 3 | 17.4 | 11.5 | -10.8 | 23.2
FLA | SLI | 110 | 1 | 5.2 | -12.9 | 14.1 | -12 | 5.1 | 10.8 | -15.6 | 6.8 | 17.2 | -0.2 | -2.5 | 2.1
FLA | TON | 110 | 1 | 4.4 | -0.5 | 5.8 | 11.5 | 3.9 | 16 | -19.9 | 2.7 | 11.3 | -16.5 | 7.8 | 8.7
FLA | SLB | 110 | 1 | -15.4 | 10.3 | 18.7 | -10.3 | -2 | 8.6 | 33.7 | -14.4 | 37 | -1.3 | 10.2 | 8.4
FRA | HAR | 110 | 1 | -3.2 | -1.3 | 3.2 | -10.2 | -6.9 | 11.5 | -4.4 | -1.4 | 4.3 | -10.8 | -6.7 | 11.9
FRA | TRN | 110 | 1 | -3.7 | 1.1 | 2.8 | -14.8 | -6.8 | 11.6 | -5.2 | 0.7 | 3.7 | -15.6 | -6.7 | 12.1
FRA | HEU | 110 | 1 | -1.8 | 0.2 | 1.3 | -9.9 | -1.6 | 7.2 | -2.6 | 0.1 | 1.8 | -10.5 | -1.8 | 7.6
FRA | INC | 110 | 1 | -4 | -0.9 | 3.8 | -14.3 | -4 | 13.9 | -5.5 | -1 | 5.3 | -15.1 | -4.3 | 14.7
FIN (I) | MCD | 110 | 1 | 3.2 | -11.8 | 10.2 | 69 | -2.9 | 58 | 22.5 | -9.7 | 20.6 | 72.9 | -1.8 | 61.3
FIN (I) | PTN | 110 | 1 | 4.5 | -2 | 6.1 | 36.5 | 5.1 | 30.9 | 11.4 | -0.9 | 14.3 | 38.5 | 5.8 | 32.7
FIN (I) | GLA | 110 | 1 | 15.2 | -0.4 | 14.5 | 66.8 | 22.6 | 57.3 | 21.1 | 2.2 | 20.2 | 70.7 | 26.7 | 61.5
FIN (I) | GRA | 110 | 1 | 22.3 | -16.4 | 23.3 | 24.8 | -16 | 24.8 | 26.3 | -11.2 | 24 | 19.1 | -13.9 | 19.8
FIN (I) | POP | 110 | 1 | 25.3 | -6.4 | 21.7 | 30.6 | -5.9 | 23.8 | 30.1 | -1.8 | 25.1 | 25.3 | -3.6 | 19.5
FIN (I) | SVN | 110 | 1 | 5 | -4.6 | 6.5 | 21.5 | 3.8 | 19 | 6.9 | -3.4 | 7.3 | 22.7 | 5.2 | 20.2
FIN (I) | MCE | 110 | 1 | - | - | - | - | - | - | 1.1 | 0.7 | 1 | 4 | 0.6 | 3.3
FTT | COO | 110 | 1 | 15.4 | -4.1 | 12.9 | 73.4 | 16.1 | 56.9 | 21.5 | -4.6 | 17.7 | 77.6 | 17.9 | 60.3
FGH | MOY | 110 | 1 | - | - | - | - | - | - | 4 | -0.8 | 3.8 | 2.2 | 14.7 | 12.1
FGH | GLR | 110 | 1 | - | - | - | - | - | - | -4 | 0.8 | 3.8 | 12.3 | -15 | 15.8
GRV | GLN | 110 | 1 | - | - | - | - | - | - | 0 | -0.1 | 0.1 | 0 | -0.1 | 0.1
GRH | GOR | 110 | 1 | - | - | - | - | - | - | -36.4 | -4.5 | 35 | -26.5 | -5.5 | 22
GRH | PLA | 110 | 1 | - | - | - | - | - | - | 36.4 | 4.5 | 35 | 26.5 | 5.5 | 22
GLA | SVN | 110 | 1 | -4 | -6.7 | 5.8 | -17.6 | -14.5 | 14.8 | -5.5 | -7.3 | 6.7 | -18.5 | -15.7 | 15.8
GRI | GRI | 110 | 1 | -8 | -0.1 | 7.6 | -32.5 | -7.4 | 27.1 | -9.1 | 0.3 | 8.7 | -32.3 | -7.6 | 27
GI | KKY | 110 | 1 | 12.2 | -12.5 | 9.8 | 58.7 | -11.7 | 28.5 | 21.1 | -7.4 | 12.6 | 91.2 | -15.4 | 44.1
GI | WAT | 110 | 1 | 15 | -9.3 | 9.9 | 9.7 | 11.5 | 7.2 | -5 | 3.5 | 3.4 | 17.3 | 4.2 | 8.5
GI | WAT | 110 | 2 | 13.6 | -8.5 | 9 | 8.8 | 10.4 | 6.5 | -4.6 | 3.1 | 3.1 | 15.7 | 3.7 | 7.7
GI | RSP | 110 | 1 | - | - | - | - | - | - | 17.3 | -4.3 | 10 | 50.7 | -20.9 | 26.1
GRA | NBY | 110 | 1 | 6.8 | -0.1 | 5.7 | -5.1 | -6.4 | 6.9 | 5.7 | 0 | 4.8 | -5.8 | -6.7 | 7.4
GRO | CKN | 110 | 1 | 0 | -20.5 | 17.1 | -32.9 | 10.9 | 28.9 | -32.9 | 5.3 | 27.8 | -32.9 | 7.3 | 28.1
GAL | SAL | 110 | 1 | 7 | -32.1 | 33.2 | 2.1 | -26 | 24.7 | 8.6 | -36.3 | 37.7 | 3.6 | -31.6 | 30
GOL | GL T | 110 | 1 | 0 | -0.2 | 0.2 | 4.5 | -3.2 | 4.5 | 4.5 | -6.6 | 7.6 | 4.5 | -6.5 | 6.5
GWE | GWE | 110 | 1 | - | - | - | 0 | -16.2 | 13.2 | - | - | - | 0 | -16.1 | 13.1
GOR | MTH | 110 | 1 | 4.8 | -7.9 | 9.4 | 39.6 | 4.9 | 33 | -33.5 | 2.6 | 33.9 | -6.1 | 5.5 | 6.8
GOR | NAV | 110 | 1 | 15.4 | -13.8 | 20.9 | 26.4 | -5.3 | 22.3 | 3.6 | -4.6 | 5.9 | 29.6 | -4.7 | 24.8
GOR | NAV | 110 | 2 | 13.4 | -11.9 | 18.1 | 22.9 | -4.4 | 19.3 | 3.2 | -3.9 | 5.1 | 25.6 | -3.9 | 21.4
GOR | NAV | 110 | 3 | 18.8 | -14.3 | 23.9 | 30.4 | -3.5 | 25.3 | 4.6 | -5 | 6.8 | 33.9 | -2.5 | 28.1
GOR (I)
GOR |  | 110 | 1 | - | - | - | - | - | - | 0 | -0.6 | 0.3 | 0 | -0.6 | 0.3
GCA | CLD | 110 | 1 | - | - | - | - | - | - | 0 | -2.1 | 1.5 | 0 | -2.3 | 1.6
GCA | CLD | 110 | 2 | - | - | - | - | - | - | 0 | -2.1 | 1.5 | 0 | -2.3 | 1.6
GCA | INC | 110 | 1 | -35.3 | -6.8 | 34.9 | -15.7 | -8.6 | 13.3 | -23.1 | -7.8 | 23.7 | -30.9 | -11.7 | 24.7
GCA | INC | 110 | 2 | -35.3 | -6.8 | 34.9 | -15.7 | -8.6 | 13.3 | -23.1 | -7.8 | 23.7 | -30.9 | -11.7 | 24.7
GCA | NAN | 110 | 1 | 5.4 | 0.2 | 4.5 | 3.5 | 0.5 | 2.7 | 5.4 | 0.3 | 4.5 | 3.5 | 0.2 | 2.6
GCA | NAN | 110 | 2 | 5.7 | 0.4 | 4.8 | 3.6 | 0.6 | 2.8 | 5.7 | 0.5 | 4.8 | 3.7 | 0.3 | 2.8
GCA | YLW | 110 | 1 | - | - | - | - | - | - | -54.7 | -28.1 | 32.9 | -75.1 | -41.3 | 38.4
CLO | MRY | 110 | 1 | 0 | -17.1 | 12.6 | -28.4 | 18.1 | 24.8 | -28.5 | 17.9 | 24.7 | -28.4 | 19.2 | 25.2
CLO | CF | 110 | 1 | -10.2 | 17.7 | 11.5 | 9.5 | 0.4 | 4.5 | -5.2 | 12.7 | 7.7 | -24.8 | 6.3 | 12.2
CLO | GL T | 110 | 1 | 7.3 | -0.1 | 3.9 | 5.3 | -0.4 | 2.4 | 17.1 | -10.2 | 10.6 | 54.8 | -8.3 | 25.5
HWN | KIN | 110 | 1 | - | - | - | - | - | - | -21.8 | -1.6 | 16.1 | 6.2 | -4.9 | 5
HWN | DFR | 110 | 1 | - | - | - | - | - | - | 21.8 | 1.6 | 21 | -6.2 | 4.9 | 5.1
HAR | RE | 110 | 1 | -8.1 | 0.2 | 7.6 | -29.3 | -9.9 | 28.9 | -11.2 | -0.7 | 10.5 | -30.9 | -10.2 | 30.4
HEU | INC | 110 | 1 | -5.8 | 2.5 | 4.5 | -19 | -1.1 | 13.6 | -8.1 | 2.2 | 6 | -20.1 | -1.4 | 14.4
IA | MAC | 110 | 1 | 3.1 | -24 | 12.3 | -21.9 | 3.5 | 10.2 | -6.9 | -0.7 | 3.5 | -3.9 | -5.1 | 2.9
INC | MIL | 110 | 1 | 9.9 | -5.6 | 9.5 | 44.9 | 0.4 | 34.2 | 13.8 | -5.4 | 12.4 | 47.4 | 1 | 36.2
INC | YLW | 110 | 1 | - | - | - | - | - | - | 73.8 | 26.2 | 41.9 | 94.2 | 38.9 | 45.7
IKE | IKE T | 110 | 1 | -6.9 | -0.3 | 8.6 | -21.2 | -12.9 | 20.8 | 1.1 | -1.2 | 2 | -23 | -8.9 | 20.7
KNR | KPG | 110 | 1 | -5.5 | 3.2 | 4.7 | -13.7 | -12.1 | 11.5 | 10.3 | 1.2 | 7.6 | -6.5 | -10.7 | 7.9
KNR | TRI | 110 | 2 | 5.5 | -3.2 | 6.4 | 13.7 | 12.1 | 15.1 | -10.3 | -1.2 | 10.5 | 6.5 | 10.7 | 10.3
KNR | KNR | 110 | 1 | 0 | 5.4 | 0.3 | 6.2 | 5.2 | 0.4 | 8.5 | 6 | 0.7 | 6.2 | 5.4 | 0.4
KNR | TRI | 110 | 1 | 0 | -19.3 | 10.9 | -43.6 | 15.2 | 22.1 | -38 | 6.3 | 21.6 | -43.6 | 14.3 | 22
KRA | MEN | 110 | 1 | - | - | - | 0 | -3.8 | 3.1 | 0 | -3.4 | 2.8 | 0 | -3.8 | 3.1
KRA | KBY | 110 | 1 | 19.2 | -18.7 | 15.1 | 26.2 | 15.9 | 14.6 | -2.3 | 2 | 1.7 | 47.2 | 13.2 | 23.3
KRA | BAR T | 110 | 1 | 30 | -18.9 | 26.1 | 65.5 | -12.1 | 41.9 | 18.2 | -7.5 | 14.5 | 73 | -16.1 | 47
KRA | MID | 110 | 1 | 3.2 | 12.7 | 13.2 | 11.5 | 10 | 12.6 | 9.9 | 6.4 | 11.9 | 8.4 | 11.4 | 11.7
KRA | WHO | 110 | 1 | 6.8 | 2.1 | 4 | 47.6 | -1.7 | 22.7 | 25.2 | -5.2 | 14.4 | 34.2 | 8.4 | 16.8
KRA | KLP | 110 | 2 | - | - | - | - | - | - | -2.2 | 0.6 | 2.3 | 35.3 | -1.4 | 29.2
KBY | MR | 110 | 2 | -15.8 | 20 | 24.7 | -12 | -4.9 | 10 | -1.1 | -2.2 | 2.4 | -34.5 | -8.1 | 27.3
KCY | CBT | 110 | 1 | - | - | - | - | - | - | -38 | -15.5 | 21.9 | -38 | -15.1 | 18.3
KCY | BKY | 110 | 1 | - | - | - | - | - | - | 14.2 | 7.4 | 8.6 | 14.2 | 7 | 7.1
KTL | MAY | 110 | 1 | -25.9 | 12.6 | 29.1 | -55.5 | 20.6 | 48.9 | -11.9 | 0.6 | 12 | -35.8 | 5.8 | 30
KTL | MON | 110 | 1 | 18.9 | -13.1 | 16.9 | 19.2 | -1.6 | 12.1 | 2.2 | -1.4 | 1.9 | -2.5 | 14.8 | 9.5
KTL | KTL | 110 | 1 | - | - | - | 0 | -33 | 26.8 | - | - | - | 0 | -32.5 | 26.4
REM | TRL | 110 | 1 | 0 | 3.2 | 2.6 | 17.1 | -23.8 | 20.8 | 10.4 | 2.2 | 8.5 | 24.8 | 0.9 | 17.6
KKY | KLS | 110 | 1 | -1.4 | -11.7 | 11.9 | -4 | 4.4 | 4.9 | -8.2 | -2.4 | 8.6 | -7.9 | -1.2 | 6.6
KKY | KKY | 110 | 1 | - | - | - | 0 | -34.3 | 27.9 | - | - | - | 0 | -32.2 | 26.2
KSE | CBT | 110 | 1 | - | - | - | - | - | - | -14.7 | -5.6 | 8.4 | -14.7 | -5.5 | 7.1
KSE | AGN | 110 | 1 | - | - | - | - | - | - | -9 | -3.2 | 5.1 | -9 | -3.2 | 4.3
LIM (I)
KLN |  | 110 | 1 | 31.7 | -5.7 | 32.5 | 47.3 | 7.3 | 39.6 | 27.2 | 2.9 | 27.6 | 41.9 | 5.6 | 34.9
KLN | CUR | 110 | 1 | 6 | -32.4 | 24.2 | -22.9 | 11.3 | 16.1 | -37.8 | 11.7 | 29.1 | -21.6 | 2.1 | 13.7
KLN | SNG | 110 | 1 | 39.3 | -18 | 24.3 | 49.8 | 4.2 | 23.9 | -4.8 | 6.1 | 4.3 | 65.1 | -12.6 | 31.7
OUG T
KER |  | 110 | 1 | 15.7 | -20.5 | 14.5 | 8.5 | -9.9 | 6.2 | 16.8 | -9.2 | 10.7 | 30.1 | -13.6 | 15.7
KUR | NAV | 110 | 1 | -23.7 | -13.1 | 27.3 | -23.7 | -13 | 21.9 | -23.7 | -13.3 | 27.4 | -23.7 | -13 | 21.9
BYH | GLE | 110 | 1 | 0.1 | -53.8 | 43.4 | -43.1 | 2.6 | 34.8 | -39.1 | -6.1 | 31.9 | -43.2 | -7.7 | 35.4
KCR | GLE | 110 | 1 | 0 | 8 | 6.6 | 31.1 | -32.3 | 36.7 | 31.1 | -24.9 | 32.7 | 31.2 | -25.2 | 32.8
KTN | WAT | 110 | 1 | -9.3 | 4.4 | 10.3 | -15.9 | -12.5 | 16.7 | 3.6 | -2.7 | 4.6 | -21.6 | -6.6 | 18.7
KLM | CRM | 110 | 2 | 0 | -1.4 | 1 | 0 | -1.6 | 1.1 | 0 | -1.4 | 1 | 0 | -1.5 | 1.1
KLM | CRM | 110 | 1 | 0 | -1.4 | 1 | 0 | -1.6 | 1.1 | 0 | -1.4 | 1 | 0 | -1.5 | 1.1
KLM | NBY | 110 | 1 | 25.5 | 2.2 | 21.5 | 37.4 | 7.2 | 32 | 26.6 | 2.8 | 22.5 | 38.1 | 7.7 | 32.7
KLM | POP | 110 | 1 | -19.5 | 0.2 | 16.2 | -9.7 | 3 | 7.8 | -22 | -3.9 | 18.6 | -3.2 | 1.1 | 2.6
KUD | CBT | 110 | 1 | - | - | - | -25.7 | -9.5 | 12.3 | -22.8 | -12 | 13.8 | -22.8 | -11.6 | 11.5
KPG | CNG | 110 | 1 | 0 | -2.7 | 1.9 | -7.9 | 6.9 | 7.5 | 0 | -2.3 | 1.6 | -20.4 | -2 | 14.7
RAT (I)
KPG |  | 110 | 1 | 11.1 | 4.5 | 8.8 | 46.1 | 4.6 | 29.2 | -0.9 | 11 | 8.1 | 24.3 | 11.3 | 16.8
KPG | TRL | 110 | 1 | 1.7 | -2.5 | 3 | 13.7 | 4 | 11.8 | -8.1 | -0.8 | 8.2 | 5.8 | 7 | 7.5
CBT | BKY | 110 | 2 | - | - | - | 10.9 | 2.7 | 5.1 | 43 | 16 | 24.5 | 43 | 15.3 | 20.5
CBT | AGN | 110 | 1 | - | - | - | - | - | - | 46.1 | 14.3 | 25.8 | 46.1 | 13.9 | 21.6
LA | MUL | 110 | 1 | -0.3 | 30.1 | 30.4 | 21.6 | -7.9 | 19 | 48.1 | -11.5 | 49.9 | 18.2 | -13.2 | 18.6
LA | RIC | 110 | 1 | 3.8 | -0.4 | 3.8 | 16.9 | 4 | 14.1 | 5.3 | -0.1 | 5.3 | 17.8 | 4.3 | 14.9
LA | RIC | 110 | 2 | 4.7 | -0.2 | 4.8 | 21 | 5.1 | 17.6 | 6.5 | 0.1 | 6.6 | 22.2 | 5.4 | 18.6
LA | SLB | 110 | 1 | 15.5 | -11.2 | 19.3 | -7 | -10.9 | 10.5 | -33.1 | 14.7 | 36.6 | -16 | -10.5 | 15.6
LOU | MLN | 110 | 1 | 10.1 | 5.3 | 11.5 | 45 | 18.7 | 40.3 | 2.6 | 3.3 | 4.3 | 33.3 | 17.6 | 31.1
LOU | RRU | 110 | 1 | 9 | -18.9 | 22 | -13.6 | -7.2 | 13.7 | -18.3 | 6.3 | 20.4 | 11.5 | -2.3 | 10.5
LOU | LOU | 110 | 1 | - | - | - | 0 | -32 | 26 | - | - | - | 0 | -33.4 | 27.1
LIM (I)
| MTN | 110 | 1 | 37.6 | 16.5 | 23.1 | 15.8 | 4.8 | 7.9 | 46.2 | 16.5 | 27.6 | -38.8 | 14.5 | 19.7
LIM (I) | RAT (I)
|  | 110 | 1 | -4.1 | -8.8 | 9.7 | -10.9 | 4.4 | 9.7 | 1.8 | -7.8 | 8.1 | 13.1 | -0.2 | 10.8
LIM (I)
| KLN | 110 | 2 | -24.7 | 4 | 31.3 | -36.8 | -5.8 | 33.9 | -21.2 | -2.7 | 26.7 | -32.6 | -4.6 | 29.9
CNB | PLS | 110 | 1 | - | - | - | - | - | - | 52.9 | -7.2 | 30 | 89.1 | -13.3 | 42.9
LIS | SKL | 110 | 1 | 1.4 | -15.3 | 15.5 | -27.5 | 5.2 | 22.8 | -6.5 | -1 | 6.6 | -1.2 | 4.1 | 3.5
LIS | LOU | 110 | 1 | -8.3 | 14.5 | 16.8 | -4.6 | 18.2 | 15.3 | 3.7 | -0.4 | 3.7 | -23.1 | 19 | 24.3
LIS | LIS | 110 | 1 | - | - | - | 0 | -0.3 | 0.1 | 0 | -0.3 | 0.2 | 0 | -0.3 | 0.1
LIS | LIS | 110 | 1 | - | - | - | 0 | -0.3 | 0.1 | 0 | -0.3 | 0.2 | 0 | -33.2 | 27
LUM | PLS | 110 | 1 | -1.4 | 21.4 | 12 | 36.6 | -5.7 | 17.7 | 18.1 | -3.1 | 10.3 | 26.4 | -3.8 | 12.7
LUM | DAL | 110 | 1 | 1.4 | -21.4 | 12 | -36.6 | 5.7 | 17.7 | -18.1 | 3.1 | 10.3 | 33.5 | -2.8 | 16
LET | LNA | 110 | 1 | - | - | - | - | - | - | -12.2 | 6.9 | 10.3 | -43.6 | 9 | 28
LET | TLK | 110 | 1 | 4.2 | -3.7 | 5.3 | -9.2 | 5.7 | 8.8 | -25.6 | 23.3 | 33 | -9.4 | 2.9 | 8
LET | GL T | 110 | 1 | -7.3 | -1.9 | 7.6 | -9.7 | 2.1 | 8.2 | -21.2 | 16.1 | 26.9 | -57.3 | 17.6 | 49.6
LET | LET | 110 | 1 | - | - | - | 0 | -16.6 | 13.5 | 0 | -31.3 | 29.8 | 0 | -16.2 | 13.2
LET | LET | 110 | 1 | - | - | - | 0 | -16.6 | 13.5 | 0 | -31.3 | 29.8 | 0 | -10.1 | 8.2
STR (N)
LET |  | 110 | 1 | -0.5 | 47.8 | 48.3 | 0 | 3 | 2.4 | 102.9 | -19 | 105.7 | 145.8 | -27.3 | 120.6
LNA | TIV | 110 | 1 | - | - | - | - | - | - | -12.2 | 7.3 | 10.4 | -34.7 | 8.6 | 22.5
LIB | MR | 110 | 1 | -3.7 | -0.6 | 5.6 | -17.3 | -5.1 | 26.6 | -5.2 | -0.9 | 7.8 | -18.3 | -5.4 | 28.1
LIB | MR | 110 | 2 | -1.9 | -0.3 | 1.9 | -8.4 | 0.3 | 7.1 | -2.6 | -0.5 | 2.7 | -8.9 | 0.2 | 7.5
LSN | THU | 110 | 1 | 0 | -0.4 | 0.4 | 29.8 | -6.4 | 25 | 29.8 | -13.9 | 31.6 | 38.4 | -13.1 | 33.3
CUR | NEN | 110 | 1 | 5.8 | 0.7 | 5.6 | 19 | 11.2 | 17.9 | 4 | 3.8 | 5.2 | 20.3 | 12.5 | 19.4
CUR | BKM | 110 | 1 | 0 | -32.8 | 17.3 | -42 | 0.5 | 22.1 | -41.9 | 7.6 | 22.4 | -42 | -10.1 | 22.7
MHL | RE | 110 | 1 | -13.5 | 4 | 10 | -46.4 | -9 | 33.7 | -18.8 | 2.6 | 13.5 | -49 | -9.6 | 35.7
MHL | TRN | 110 | 1 | 6.5 | -4.2 | 5.6 | 26.3 | 6 | 19.2 | 9.1 | -3.1 | 6.9 | 27.8 | 6.2 | 20.3
MCE | CDU | 110 | 1 | -7.9 | -2 | 8.3 | -19.2 | -2.4 | 15.6 | -11.2 | -1.9 | 11.6 | -25 | -1.5 | 20.2
MCD | WOL | 110 | 1 | 11.9 | 1.2 | 9.9 | 26.4 | 6.9 | 20.8 | 11.3 | 2.2 | 9.6 | 27.9 | 7.4 | 22
MTH | LOU | 110 | 1 | -4.9 | -8.1 | 9.5 | -4.8 | -23.3 | 19.7 | -27.5 | -0.6 | 27.8 | -46.5 | -15.4 | 40.5
MAY | TIM | 110 | 1 | - | - | - | - | - | - | 9.8 | -1.1 | 8.8 | 18.5 | -1.4 | 16.5
MAY | GRI | 110 | 1 | 8 | -0.1 | 8.1 | 32.5 | 7.3 | 27.8 | 9.1 | -0.6 | 9.2 | 32.4 | 7.5 | 27.7
MAY | GRI | 110 | 1 | 8 | -0.1 | 8.1 | 32.5 | 7.3 | 27.8 | 9.1 | -0.6 | 9.2 | 32.6 | 7.1 | 27.2
MAY | RYB | 110 | 1 | 97.5 | 30.8 | 57.4 | 123.7 | 19 | 57.2 | 102.1 | 31.1 | 59.9 | 82.2 | 20.1 | 38.7
MAY | RNW | 110 | 1 | 13.8 | -9.9 | 21.1 | 20.3 | 4.4 | 20.2 | -9.3 | -0.9 | 11.7 | 27.2 | -0.3 | 26.4
MAY | BLK T | 110 | 1 | -2.5 | -9.1 | 9.6 | 37.5 | -7.7 | 31.7 | -30.5 | 0.7 | 30.8 | 9.6 | 6.4 | 9.5
MIL | RE | 110 | 1 | -5.4 | -0.7 | 5.4 | -21.8 | -2.7 | 22 | -7.5 | -0.7 | 7.5 | -23.1 | -3 | 23.3
MIL | RE | 110 | 2 | -4.4 | 0.5 | 3.7 | -17.2 | -1.9 | 13.2 | -6 | 0.3 | 5 | -18.1 | -2.2 | 13.9
MAC | CLA | 110 | 2 | 1.7 | -35.3 | 22 | -42.2 | -2.6 | 22 | -10.4 | -0.8 | 6.5 | -11.9 | -8.7 | 7.7
MTN | MUN | 110 | 1 | 10.8 | 6.6 | 28 | 10.8 | 6.6 | 28 | 10.8 | 6.7 | 28.1 | 10.8 | 6.6 | 28.1
MTN | MUN | 110 | 2 | 10.8 | 6.6 | 28 | 10.8 | 6.6 | 28 | 10.8 | 6.7 | 28.1 | 10.8 | 6.6 | 28.1
MP | TBK T | 110 | 1 | 21 | -4.8 | 12.1 | 45.2 | 14.4 | 22.6 | -11 | 4.6 | 6.7 | 8.8 | 12.6 | 7.3
MR | TBG | 110 | 1 | -19.2 | 20.2 | 15.6 | -31.4 | -6.1 | 14.6 | -6.3 | 1.1 | 3.6 | -47.5 | -4.1 | 21.8
MR | TBG | 110 | 2 | -22.3 | 24 | 18.4 | -36.4 | -6.5 | 16.9 | -7.3 | 1.9 | 4.2 | -55.1 | -4.2 | 25.2
MR | KLP | 110 | 1 | - | - | - | - | - | - | 0 | -3.1 | 2.6 | 22.3 | -3.5 | 18.8
MAL | KLP | 110 | 1 | - | - | - | - | - | - | -14.7 | 0.8 | 11 | -63.8 | 2.8 | 40.1
MOY | TAW | 110 | 1 | 0 | -0.5 | 0.8 | -5.7 | 9.5 | 16.3 | 0 | -0.4 | 0.7 | -9 | 0.1 | 13.2
MOY | TAW | 110 | 2 | 0 | -0.5 | 0.7 | 0 | 6.8 | 10 | 0 | -0.4 | 0.6 | 0 | -0.4 | 0.6
MOY | TON | 110 | 1 | - | - | - | - | - | - | 22.6 | 1.3 | 12.7 | 29 | -1.5 | 13.8
BCT | CKM | 110 | 1 | -49.7 | -17.3 | 37.6 | -49.7 | -16.2 | 37.3 | -49.7 | -17.5 | 37.7 | -49.7 | -16.6 | 37.4
NEW (I)
| BLK T | 110 | 1 | 8.5 | 7.6 | 8.4 | -10.6 | 13.8 | 11 | 37.7 | -0.7 | 27.7 | 18.6 | -1.6 | 11.7
NQS | RE | 110 | 1 | -7 | -0.2 | 5.9 | -24.6 | -4.6 | 21 | -9.8 | -0.4 | 8.2 | -25.9 | -5.1 | 22.2
OUG T
OUG |  | 110 | 1 | -7.5 | 0.9 | 7.2 | -24.9 | -5.2 | 20.7 | -8.4 | 1.2 | 8.1 | -26.4 | -4.4 | 21.8
PA | STR T | 110 | 1 | 0 | -0.8 | 1.2 | 30 | -12.7 | 47.9 | 34 | -21.5 | 59.2 | 34 | 3.9 | 50.3
PHY | SHE | 110 | 1 | - | - | - | - | - | - | 2.3 | 0.7 | 1.4 | 2.3 | 0.7 | 1.1
PB | RE | 110 | 3 | 33.8 | -30 | 16.8 | 125.6 | -14.7 | 47 | 47 | -27.6 | 20.3 | 132.7 | -0.2 | 49.3
PB | RE | 110 | 4 | 32.8 | -29.1 | 16.3 | 121.8 | -14.2 | 45.6 | 45.6 | -26.7 | 19.7 | 128.7 | -0.1 | 47.9
PLA | OBE | 110 | 1 | - | - | - | - | - | - | 18.3 | -2.2 | 17.5 | 8.4 | -1 | 6.8
RE | WBK | 110 | 1 | 0 | -2.2 | 1.8 | 0 | -27 | 19.1 | 0 | -2.1 | 1.7 | 0 | -2.3 | 1.7
RAF | TBG | 110 | 1 | 25.8 | -30.9 | 20.7 | 61.5 | 4 | 2.8 | 11.7 | -5.7 | 6.7 | 82.2 | -1 | 3.7
RAF | TBG | 110 | 2 | 35.2 | -20.7 | 22.9 | 81.1 | 14.9 | 39.4 | 28.6 | -4.5 | 16.3 | 100 | 19 | 48.7
RNW | DFR | 110 | 1 | 4.6 | -11.3 | 12.3 | 11.1 | 3 | 9.5 | -18.5 | -2.4 | 18.8 | 18 | -1.8 | 15
RRU | SKL | 110 | 1 | 8.8 | -17.7 | 20.8 | 10.1 | 8.6 | 11.8 | 5.2 | -10.2 | 12.1 | 35.2 | -8.9 | 32.4
SH | DLN | 110 | 1 | - | - | - | - | - | - | 0 | -4 | 2.8 | 0 | -4.2 | 3
SH | DAL | 110 | 1 | -1.4 | 19.6 | 11.1 | 49.9 | 1.2 | 23.8 | 19.6 | -2.3 | 11.1 | -19.3 | 10.3 | 10.4
SH | IKE T | 110 | 1 | -1.6 | 8.5 | 4.9 | -18.5 | 8.6 | 9.7 | -25 | 9.1 | 14.9 | -27.2 | 8.3 | 13.5
SOM T
SH |  | 110 | 1 | 5.8 | -22.6 | 22.2 | -7.2 | 3.1 | 6.4 | -21.5 | 7.2 | 21.6 | 12.9 | -4.6 | 11.1
SLI | SRA | 110 | 1 | -3.2 | 2.2 | 4 | -14.7 | 2.1 | 12.3 | -1.6 | 4.9 | 5.2 | -6.1 | -0.7 | 5
SLI | SRA | 110 | 2 | -3 | 2 | 3.6 | -13.6 | 2 | 11.3 | -1.4 | 4.5 | 4.8 | -5.6 | -0.7 | 4.7
SLI | SLI | 110 | 1 | - | - | - | 0 | -16.4 | 13.3 | - | - | - | 0 | -16.5 | 13.4
SOR | TLK | 110 | 1 | 0 | -0.3 | 0.2 | 18.8 | 3.3 | 15.5 | 18.1 | -17.2 | 23.8 | 20.2 | 5.8 | 17.1
SOM T
SOM |  | 110 | 1 | -2.2 | 0.8 | 2.2 | -21.5 | -5.5 | 18 | -0.8 | 0.5 | 0.9 | -22.8 | -4.6 | 18.9
SRA | CF | 110 | 2 | 17.6 | -16.1 | 13.4 | -9.2 | -1.4 | 4.4 | -11.6 | 6.7 | 7.5 | 27.3 | -4.9 | 13.2
STR | STR T | 110 | 1 | -3.6 | -0.1 | 8.1 | -24.3 | -5.7 | 55.4 | -5 | -0.1 | 11.2 | -25.7 | -6.3 | 58.7
SNG | AA | 110 | 1 | 35.3 | -18.1 | 27.4 | 31.5 | 0.7 | 17.8 | -10.2 | 6.1 | 8.2 | 45.7 | -16.6 | 27.5
SBH | CDU | 110 | 1 | -16.5 | -5.1 | 12.6 | -22.8 | -5.3 | 17.1 | -59.5 | -24.5 | 47 | -59.5 | -23.9 | 46.8
SOM T
SHN |  | 110 | 1 | -3.3 | 19.9 | 19.2 | 29.3 | 1.2 | 23.8 | 22.8 | -8.8 | 23.3 | 10.1 | 7.1 | 10
TIV | MLG | 110 | 1 | - | - | - | - | - | - | 0 | -6.3 | 4.5 | -9 | -6.7 | 8
CNN | CLO | 110 | 1 | 0 | 18.4 | 10.3 | 0 | 15.5 | 7.4 | 0 | 14.3 | 8.1 | 41.3 | 12.5 | 20.5
CNN | CAG | 110 | 1 | 0 | -10.3 | 7.4 | 0 | -8.7 | 6.2 | 0 | -8 | 5.7 | -41.3 | -5.6 | 29.7
CNN | CDF | 110 | 1 | 0 | -8.1 | 5.8 | 0 | -6.8 | 4.9 | 0 | -6.3 | 4.5 | 0 | -6.9 | 4.9
TBK | TBK T | 110 | 1 | -1.3 | 1 | 1.6 | -3.7 | -7.7 | 6.9 | 7.4 | 0.1 | 7.1 | -4.4 | -3.5 | 4.6
CTN | KLN | 110 | 1 | 5 | -20.8 | 12 | 0.5 | -3 | 1.5 | 11 | 0.8 | 6.2 | 25.1 | 2.6 | 12
CTN | TIP | 110 | 1 | -5 | 32.2 | 18.3 | 52 | -14.8 | 25.7 | 21.3 | 4.5 | 12.2 | 27.5 | 1 | 13.1
OUG T
TRL |  | 110 | 1 | -8.1 | 18.2 | 11.2 | 16.5 | 13.9 | 10.3 | -8.3 | 6.7 | 6 | -3.4 | 17.4 | 8.5
THU | IKE T | 110 | 1 | 8.6 | -11.2 | 7.9 | 40.1 | 3.2 | 19.1 | 24.2 | -9 | 14.5 | 50.8 | 0.8 | 24.2
THU | THU | 110 | 1 | - | - | - | 0 | -16.5 | 13.4 | - | - | - | 0 | -16.5 | 13.4
RSP | WEX | 110 | 1 | - | - | - | - | - | - | 17.3 | -3.5 | 9.9 | 50.3 | -21.6 | 26.1
WEX | WEX | 110 | 1 | - | - | - | 0 | -34.2 | 27.8 | - | - | - | 0 | -32.6 | 26.5
CTG | BVK | 110 | 1 | 0 | 1 | 0.5 | 46.5 | -45.5 | 28.5 | 18.7 | 0.2 | 8.2 | 46.6 | -2.1 | 20.5
WHO | KMA | 110 | 1 | 0 | -1.6 | 1.3 | -10.2 | 2.8 | 8.5 | 0 | -1.5 | 1.2 | -10.2 | -1.5 | 8.3
BK | SKY | 110 | 1 | 0 | -5.7 | 3 | -51.2 | 17.3 | 24.2 | -51.3 | 1.2 | 27.4 | -51.3 | 0.8 | 23
BK | CRN | 110 | 1 | 0 | -0.2 | 0.1 | 0 | -0.1 | 0.1 | -0.5 | 13.5 | 7.6 | -14.9 | 27.2 | 14.8
CKM | FAS | 110 | 1 | 5.5 | 1.7 | 5.5 | 30.8 | 12.2 | 27 | 7.7 | 2.5 | 7.7 | 32.6 | 13.6 | 28.7
BKM | CUR | 110 | 1 | 0 | -9 | 7.5 | -28.1 | 11.6 | 25.3 | -28.1 | 25.6 | 31.7 | -28.1 | 10.1 | 24.9
ENN (N)
AGH |  | 110 | 1 | -2.6 | 5.2 | 5.3 | 2.9 | 6.9 | 6 | 1.2 | 1.7 | 1.9 | -17.3 | 1.6 | 14
AIR | ROS | 110 | 1 | - | - | - | - | - | - | -5.6 | -0.9 | 6.9 | -19 | -3.6 | 18.8
AIR | ROS | 110 | 1 | - | - | - | - | - | - | -5.6 | -0.9 | 6.9 | -19 | -3.6 | 18.8
ANT | KEL | 110 | 1 | -4.5 | 5.7 | 8.9 | -20.1 | 1.7 | 19.6 | -6.1 | 4.4 | 9.2 | -21.8 | 1.6 | 21.2
ANT | KEL | 110 | 2 | -5.3 | -6 | 9.7 | -21.3 | -9.1 | 22.5 | -6.8 | -6.4 | 11.4 | -22.9 | -9.7 | 24.1
BPS | BVG | 110 | 1 | 7.1 | 1.3 | 8.8 | 4.4 | 12.3 | 12.6 | 8.8 | 3.5 | 11.6 | 55.4 | -4 | 53.9
BPS | BVG | 110 | 2 | 7.1 | 1.3 | 8.8 | 4.4 | 12.3 | 12.6 | 8.8 | 3.5 | 11.6 | 55.4 | -4 | 53.9
BPS | EDE | 110 | 1 | 14 | -21.9 | 37.7 | 40.7 | -15.2 | 50.5 | 8.2 | 1.5 | 5.8 | 30.9 | 5.1 | 18.9
BPS | EDE | 110 | 2 | 14 | -22 | 37.3 | 40.8 | -15.3 | 50.1 | 8.2 | 1.5 | 5.8 | 31 | 5.1 | 18.9
BMA | KEL | 110 | 1 | -9.7 | -1.6 | 9 | -32.1 | -9.4 | 27 | -10.6 | -0.5 | 9.7 | -45.6 | -10.8 | 37.8
BMA | KEL | 110 | 2 | -14.3 | -0.9 | 13.1 | -35.9 | -8.4 | 29.7 | -10.2 | -0.4 | 9.4 | -44.2 | -10 | 36.5
BAN | TAN | 110 | 1 | -5.6 | -1.6 | 7.1 | -19.2 | -4.6 | 19.2 | -6 | -1.7 | 7.6 | -20.5 | -5.1 | 20.5
BAN | TAN | 110 | 2 | -5.9 | -1.7 | 7.5 | -20.1 | -5.1 | 20.1 | -6.3 | -1.8 | 7.9 | -21.4 | -5.7 | 21.5
BVG | KEL | 110 | 1 | 0.7 | -1.3 | 1.3 | -15.2 | 5.5 | 13 | 2.7 | 0 | 2.4 | 30.5 | -12.1 | 26.5
BVG | KEL | 110 | 2 | 0.7 | -1.3 | 1.4 | -15.8 | 5.8 | 13.6 | 2.8 | 0 | 2.5 | 31.9 | -12.6 | 27.6
BVG | LAR | 110 | 1 | 6.4 | 3.3 | 9.1 | 19.8 | 7.2 | 18.6 | 6.1 | 4 | 9.2 | 23.5 | 7.3 | 21.8
BVG | LAR | 110 | 2 | 6.4 | 3.3 | 9.1 | 19.9 | 7.2 | 18.7 | 6.1 | 4 | 9.2 | 23.6 | 7.3 | 21.8
BNH | CAS | 110 | 1 | -8.3 | -1 | 10.2 | -28.5 | -5.7 | 28.2 | -8.9 | -1 | 10.9 | -30.3 | -6.1 | 30
BNH | CAS | 110 | 2 | -8.4 | -0.9 | 10.3 | -28.5 | -5.7 | 28.3 | -8.9 | -1 | 10.9 | -30.4 | -6.1 | 30.1
BNM | DON | 110 | 1 | -7.3 | -0.2 | 9.8 | -25 | -4.2 | 31 | -14 | 13.4 | 13.4 | -8.2 | 4.2 | 6.4
BNM | DON | 110 | 2 | -7.4 | -0.4 | 9.8 | -25.2 | -4.4 | 31.2 | -14 | 9.7 | 11.8 | -8.5 | 0.4 | 5.9
AGI | BRO | 110 | 1 | - | - | - | - | - | - | 4.8 | -10.1 | 7.8 | 0 | -0.5 | 0.3
AGI | RSK | 110 | 1 | - | - | - | - | - | - | 13.7 | -9.8 | 9 | 0 | 0.5 | 0.3
CAR | EDE | 110 | 1 | -8.7 | 22.9 | 35.5 | -23.1 | 19.3 | 35.1 | -2.9 | -0.7 | 4.3 | -12.2 | -1.3 | 14.3
CAR | EDE | 110 | 2 | -8.7 | 23 | 35.7 | -23.2 | 19.5 | 35.2 | -2.9 | -0.7 | 4.3 | -12.2 | -1.3 | 14.3
CAS | CRE | 110 | 1 | 18.7 | -7.6 | 15.3 | 64.1 | 2.1 | 44.3 | 11.9 | 4.6 | 9.6 | 80.1 | 7.3 | 55.5
CAS | CRE | 110 | 2 | 18.7 | -7.6 | 15.3 | 63.9 | 2 | 44.1 | 11.8 | 4.5 | 9.6 | 79.9 | 7.3 | 55.3
CAS | KNO | 110 | 1 | 9.2 | -3.6 | 15 | 31.6 | 2.4 | 43.4 | 8.6 | -3.2 | 13.9 | 29.5 | 1.6 | 40.5
CAS | KNO | 110 | 2 | 9.2 | -3.5 | 15 | 31.6 | 2.4 | 43.4 | 8.6 | -3.1 | 13.9 | 29.5 | 1.7 | 40.5
CAS | NAR | 110 | 1 | 6.5 | -6.1 | 8.2 | 23 | -6.1 | 19.2 | 7.2 | -5.1 | 8 | 24.5 | -5.7 | 20.3
CAS | NAR | 110 | 2 | 6.3 | -6 | 8 | 22.6 | -6.1 | 18.9 | 7 | -5 | 7.9 | 24 | -5.8 | 19.9
RAT (N)
CAS |  | 110 | 1 | 8.3 | 0.2 | 10.1 | 28.5 | 3.7 | 27.9 | 8.8 | 0.4 | 10.8 | 30.4 | 4 | 29.7
RAT (N)
CAS |  | 110 | 2 | 8.7 | 0.4 | 10.6 | 29.9 | 4.2 | 29.3 | 9.3 | 0.6 | 11.3 | 31.8 | 4.5 | 31.2
CAS | ROS | 110 | 1 | 4.4 | -0.7 | 3.1 | 12.5 | 3.3 | 8.5 | 7.2 | 1.4 | 5.1 | 28.6 | 6.4 | 19.3
CAS | ROS | 110 | 2 | 4.5 | -0.7 | 3.2 | 12.7 | 3.4 | 8.6 | 7.2 | 1.5 | 5.1 | 28.8 | 6.4 | 19.4
CEN | CEN | 110 | 1 | - | - | - | - | - | - | 0 | -1.8 | 1 | -0.1 | -1.9 | 0.9
CEN | CRE | 110 | 1 | -7.8 | -0.5 | 5.4 | -26.6 | -2.8 | 18.6 | -2.2 | -11.9 | 8.4 | -47 | -9.3 | 33.3
CEN | CRE | 110 | 2 | -7.8 | -0.5 | 5.4 | -26.6 | -2.8 | 18.6 | -2.3 | -11.8 | 8.4 | -47.1 | -9.3 | 33.3
COL (N)
| CPS | 110 | 1 | -16.5 | -1.5 | 20.2 | -24.2 | -9.3 | 25.1 | -17.6 | -2.7 | 21.7 | -39.3 | -7.1 | 38.8
COL (N) | LIM (N)
|  | 110 | 1 | -11.5 | -1 | 14.1 | -15.1 | -5.2 | 15.5 | -14.6 | -0.7 | 17.9 | -22 | -3.1 | 21.6
COL (N)
| LOG | 110 | 1 | 5.8 | -0.1 | 7.1 | 18.4 | 4.4 | 18.4 | 5.7 | 0.4 | 7 | 21.1 | 5.1 | 21
COL (N)
| LOG | 110 | 2 | 5.7 | -0.1 | 6.9 | 18 | 4.3 | 18 | 5.6 | 0.4 | 6.8 | 20.7 | 5 | 20.6
COL (N)
| RSK | 110 | 1 | 4 | 3 | 2.7 | -7.9 | -2.3 | 4.3 | 18.4 | -4.2 | 10.2 | -26.3 | -5.4 | 13.9
CPS | CLM | 110 | 1 | - | - | - | - | - | - | -3.7 | -7.6 | 4.2 | 0 | -15.1 | 7.5
CPS | KMT | 110 | 1 | 21.2 | -31.5 | 26.6 | -2.4 | 13.8 | 8.5 | -19.4 | 16.7 | 17.9 | -3.9 | 6.9 | 4.8
LIM (N)
CPS |  | 110 | 1 | 18.9 | 0.4 | 23.1 | 29.1 | 10.9 | 30.2 | 18.8 | 2.9 | 23.2 | 49.4 | 10.7 | 49.1
CPS | LMR | 110 | 1 | 4.8 | 0.5 | 5.9 | 14.2 | 3.4 | 14.2 | 4.4 | 1.1 | 5.5 | 17.5 | 3.9 | 17.4
CPS | LMR | 110 | 2 | 4.8 | 0.5 | 5.9 | 14.2 | 3.4 | 14.2 | 4.4 | 1.1 | 5.5 | 17.6 | 3.9 | 17.5
CPS | SPR | 110 | 1 | 7 | -0.5 | 8.5 | 23.9 | 2.8 | 23.3 | 7.4 | -0.3 | 9.1 | 25.4 | 3.1 | 24.8
CPS | SPR | 110 | 2 | 7 | -0.6 | 8.5 | 23.9 | 2.7 | 23.3 | 7.4 | -0.4 | 9.1 | 25.4 | 3 | 24.8
STR (N)
CPS |  | 110 | 1 | 29 | -37.6 | 43.6 | 19.8 | 11.7 | 18.5 | -20.7 | 20.9 | 27 | -3.3 | 25.2 | 20.5
CLM | AGT | 110 | 1 | - | - | - | - | - | - | 3.7 | -6.6 | 3.8 | 0 | -5.5 | 2.8
CRG | TGW | 110 | 1 | - | - | - | - | - | - | -11.7 | 3.2 | 11.1 | -16.1 | 4 | 13.4
CRG | TMN | 110 | 1 | -6.1 | -12.6 | 12.8 | -22.6 | -0.6 | 18.2 | 4.4 | -5.5 | 6.5 | -10.4 | -8.2 | 10.7
DON | HAN | 110 | 1 | -15.5 | 1.2 | 10.8 | -53 | -3.9 | 33.7 | -21.1 | 11.5 | 16.7 | -32.4 | 1.7 | 20.5
DON | HAN | 110 | 2 | -12.6 | 7.9 | 10.3 | -43.1 | 2.6 | 27.3 | -20.7 | 15.5 | 18 | -31.7 | 5.8 | 20.4
FIN (N)
DON |  | 110 | 1 | -6.2 | 6.7 | 13.2 | -22.2 | 4.8 | 26.4 | -5.5 | 6.4 | 12.3 | -19.7 | 5.8 | 23.9
FIN (N)
DON |  | 110 | 2 | -7.2 | -9 | 16.6 | -23.6 | -9.6 | 29.6 | -6.4 | -8.5 | 15.4 | -21.1 | -9.7 | 27
DRO (N)
| CRR | 110 | 1 | 0 | -1 | 0.6 | -20.2 | 0.4 | 10.1 | -16.1 | 3.3 | 8.8 | 0 | -4.5 | 2.3
DRO (N) | ENN (N)
|  | 110 | 1 | 11.1 | -13.5 | 21.3 | 20.9 | 1.8 | 20.4 | 8.9 | -4.7 | 12.3 | 22.3 | 1.4 | 21.7
DRO (N) | ENN (N)
|  | 110 | 2 | 11.1 | -13.5 | 21.3 | 20.9 | 1.8 | 20.4 | 8.9 | -4.7 | 12.3 | 22.3 | 1.4 | 21.7
DRO (N)
| OMA | 110 | 1 | -11.1 | 14 | 21.8 | -10.8 | -2 | 10.7 | -0.9 | 3.1 | 1.6 | -22.3 | 0.9 | 9.9
DRO (N)
| OMA | 110 | 2 | -11.1 | 14 | 21.8 | -10.8 | -2 | 10.7 | -0.9 | 3.1 | 1.6 | -22.3 | 0.9 | 9.9
DRU (N)
| TAN | 110 | 1 | -5 | -0.9 | 6.4 | -13.3 | -19.9 | 21.2 | 4.7 | -12.2 | 16.6 | -13.3 | -25.6 | 25.6
DRU (N)
| TAN | 110 | 2 | -5 | -0.9 | 6.4 | -13.3 | -19.9 | 21.2 | 4.7 | -12.2 | 16.6 | -13.3 | -25.6 | 25.6
DRU (N)
| TAN | 110 | 3 | -5.3 | -0.7 | 4.9 | -14.9 | -20.3 | 20 | 4.4 | -13 | 12.7 | -15.1 | -26.3 | 24
DRU (N)
| TMN | 110 | 1 | -5.7 | 0.5 | 5.3 | -24.3 | 17.8 | 24.3 | -20.7 | 17.4 | 24.8 | -27.7 | 25.6 | 30.4
DRU (N)
| TMN | 110 | 2 | -6 | 0.3 | 5.5 | -25.4 | 18.2 | 25.2 | -21.7 | 17.9 | 25.8 | -29 | 26.4 | 31.6
CRR | CRR | 110 | 1 | - | - | - | - | - | - | -4.2 | 0.2 | 5.3 | 0 | -1.6 | 3.3
CRR | PGN | 110 | 1 | - | - | - | - | - | - | -5.2 | -0.6 | 8.6 | 0 | -2 | 3.3
DUN | TMN | 110 | 1 | -11.2 | 3 | 7.4 | -29 | -13.7 | 18 | 0.2 | -7.8 | 5 | -43.1 | -16.3 | 25.9
DUN | TMN | 110 | 2 | -7.5 | 3.1 | 5.6 | -21.4 | -6.9 | 15.6 | -0.5 | -5.4 | 3.8 | -31.4 | -7.5 | 22.4
DUN | OMA | 110 | 1 | 0.2 | -14.7 | 7.9 | -17.1 | 0 | 8.9 | -28.8 | 11.5 | 16.7 | 7.5 | 3.1 | 4.2
DUN | TMN | 110 | 3 | -10 | 1.2 | 5.4 | -24.7 | -14.3 | 14.8 | 0.6 | -7.5 | 4.1 | -36.9 | -17.2 | 21.1
ENN (N) | ENN (N)
|  | 110 | 1 | 0.3 | -2.7 | 2.2 | 1.7 | 0.5 | 1.4 | 6 | 3.5 | 5.6 | -35.3 | -3.3 | 28.4
FIN (N)
| HAN | 110 | 1 | -11.7 | -8.9 | 10.2 | -39.1 | -11.1 | 28.2 | -11.3 | -8.5 | 9.8 | -37.7 | -11.2 | 27.3
FIN (N)
| HAN | 110 | 2 | -10.7 | 6.6 | 8.7 | -37.6 | 3.2 | 26.2 | -10.3 | 6.2 | 8.4 | -36.2 | 4.1 | 25.3
GLE (N)
| KEL | 110 | 1 | -6.6 | -1.8 | 8.3 | -22.5 | -7 | 26.2 | -4.8 | -1.1 | 6 | -16.4 | -4.3 | 18.8
GLE (N)
| KEL | 110 | 2 | 0 | -3 | 3.6 | 0 | -2.9 | 3.2 | -4.8 | -1.1 | 6 | -16.4 | -4.3 | 18.8
GOR (N)
| OMA | 110 | 1 | 2.7 | -6.2 | 3.4 | 4.7 | 0.6 | 2.4 | -12.1 | 3.2 | 6.3 | 8.1 | 7.8 | 5.6
GOR (N)
| TMN | 110 | 1 | -2.7 | 10.4 | 5.4 | 15.5 | 0.2 | 7.7 | 24.1 | -6 | 12.4 | -8.1 | -4 | 4.5
LIS (N)
HAN |  | 110 | 1 | -7.7 | -17.1 | 22.8 | -4.1 | 2.5 | 4.7 | 13.7 | -2.6 | 17 | 9.1 | 2.9 | 9.2
LIS (N)
HAN |  | 110 | 2 | -8 | -18.2 | 24.9 | -6.5 | 1.3 | 6.7 | 13.8 | -2.4 | 17.5 | 7.2 | 2 | 7.5
KEL | KLC | 110 | 1 | - | - | - | - | - | - | 0 | -1.1 | 0.8 | 0 | -1.2 | 0.8
KEL | RSK | 110 | 1 | -7.4 | -13.4 | 8.3 | -22.5 | 4.2 | 11.9 | -10.1 | 2.1 | 5.6 | 10 | -3.1 | 5.4
KEL | RSK | 110 | 2 | - | - | - | - | - | - | -10.6 | 0.9 | 5.6 | 10.4 | -1.9 | 5
KEL | TGW | 110 | 1 | - | - | - | - | - | - | -5 | -1.9 | 2.7 | 22.4 | -6.4 | 11.6
KLC | KLC | 110 | 1 | - | - | - | - | - | - | 0 | -0.3 | 0.2 | 0 | -0.3 | 0.2
KMT | SLK | 110 | 1 | 0.1 | -22.5 | 20.6 | -21.8 | 11.7 | 19.9 | -7.2 | 6.4 | 8.9 | 0.1 | -20.8 | 16.8
STR (N)
KMT |  | 110 | 1 | 21.1 | -9 | 16 | 30.1 | 3.3 | 18.2 | -8.7 | 6.2 | 7.4 | -4 | 28.2 | 17.2
LIS (N)
| TAN | 110 | 1 | -15.6 | -13.5 | 25.1 | -41.3 | -2.8 | 40.2 | 2.1 | -1.4 | 3 | -30.7 | -2.9 | 29.9
LIS (N)
| TAN | 110 | 2 | -16 | -14.8 | 27.2 | -43.6 | -4.2 | 43.8 | 2.3 | -1.2 | 3.2 | -32.3 | -3.9 | 32.5
MKL | OMA | 110 | 1 | 0 | 1.1 | 0.8 | 41.3 | 5.7 | 26.6 | 13.8 | -14.5 | 14.4 | 0 | 1 | 0.6
NEW (N)
| TAN | 110 | 1 | -11.7 | -2 | 14.5 | -40 | -9.7 | 40 | -12.5 | -2.2 | 15.4 | -42.7 | -10.1 | 42.5
NEW (N)
| TAN | 110 | 2 | -11.7 | -2 | 14.5 | -40.1 | -9.7 | 40.1 | -12.5 | -2.2 | 15.5 | -42.8 | -10.1 | 42.6
STR (N)
OMA |  | 110 | 1 | -18 | 0.8 | 16.6 | -7.8 | -4.5 | 7.3 | -29.3 | 4.8 | 27.3 | -42.1 | 6.7 | 34.4
STR (N)
OMA |  | 110 | 2 | -17.7 | 0.8 | 21.6 | -7.7 | -4.5 | 8.6 | -28.9 | 4.7 | 35.7 | -41.4 | 6.6 | 40.7
OMA | TRE | 110 | 1 | -1.5 | 8.2 | 4.5 | -1.5 | -2.4 | 1.5 | 19.4 | -9.7 | 11.7 | -10.7 | -7.6 | 6.8
RSK | TGW | 110 | 1 | - | - | - | - | - | - | 16.8 | -5.6 | 8.8 | -6.1 | -1.9 | 3.2
STR (N) | STR (N)
|  | 110 | 1 | 1.2 | -46.6 | 37.3 | 0 | -3.7 | 3 | -99 | 31.3 | 83.1 | -138.2 | 52.1 | 118.2
TAN | WAR | 110 | 1 | 9.3 | 1.4 | 11.9 | 33.3 | 8.3 | 30.4 | 10.3 | 1.9 | 13.3 | 35.4 | 8.7 | 32.3
TAN | WAR | 110 | 2 | 9.3 | 1.4 | 11.8 | 33.3 | 8.2 | 30.3 | 10.3 | 1.9 | 13.3 | 35.4 | 8.7 | 32.2
TRE | TMN | 110 | 1 | -1.5 | 13.2 | 7.2 | 21.5 | -1.7 | 11.2 | 27 | -10.8 | 15.6 | -10.8 | -3.1 | 5.8

## generator
Generator Technical Data - PUBLIC
Plant ID | [6 empty] | Fuel type |  |  |  |  | Capacity |  |  | Heat Rate Curve | [10 empty] | Forced Outages |  | TOD |  |  |  | Starts
Company Name | Jurisdiction | SEM Unit ID | Plexos Unit ID | Unit Name | bus name | Change Date for New Unit Characteristics | Start Fuel 1 | Percent 1 | Start Fuel 2 | Percent 2 | Fuel for Generation and No Load | Min Stable Capacity (MW) | Max Capacity (MW) | Summer Rating--Where Different (MW) | No Load Heat Requirement (GJ/hr) | Capacity point 1 (MW) | Capacity point 2 (MW) | Capacity point 3 (MW) | Capacity point 4 (MW) | Capacity point 5 (MW) | Heat Rate Inc 1 (GJ/MWh) | Heat Rate Inc 2 (GJ/MWh) | Heat Rate Inc 3 (GJ/MWh) | Heat Rate Inc 4 (GJ/MWh) | Heat Rate Inc 5 (GJ/MWh) | Forced Outage Rate,% | Mean Time to Repair, hrs | Ramp Rate Up, MW/min | Ramp Rate Down, MW/min | Min Up Time (hrs) | Min Down Time (hrs) | Start up Energy (GJ) Hot | Start up Energy (GJ) Warm | Start up Energy (GJ) Cold | Hot to Warm boundary, hrs | Warm to Cold boundary, hrs
ESB | ROI | GU_400200 | AA1 | Ardnacrusha 1 | Ardnacrusha |  | Water | 100% |  |  | Water | 0 | 21 | [12 empty] | 4.5% | 86 | 0.42 | 0.42
ESB | ROI | GU_400201 | AA2 | Ardnacrusha 2 | Ardnacrusha |  | Water | 100% |  |  | Water | 0 | 22 | [12 empty] | 4.5% | 86 | 0.47 | 0.47
ESB | ROI | GU_400202 | AA3 | Ardnacrusha 3 | Ardnacrusha |  | Water | 100% |  |  | Water | 0 | 19 | [12 empty] | 4.5% | 86 | 0.33 | 0.33
ESB | ROI | GU_400203 | AA4 | Ardnacrusha 4 | Ardnacrusha |  | Water | 100% |  |  | Water | 0 | 24 | [12 empty] | 4.5% | 82 | 0.55 | 0.55
ESB | ROI | GU_400850 | ADC | Aghada CCGT | Aghada |  | Gas | 100% |  |  | Gas | 130 | 440 |  | 589.4 | 130 | 200 | 320 | 380 | 440 | 3.177 | 5.297 | 5.393 | 5.757 | 5.814 | 6.2% | 192 | 8.83 | 12.38 | 4 | 4 | 1200 | 1200 | 1200 | 12 | 60
ESB | ROI | GU_400181 | AT1 | Aghada CT 1 | Aghada |  | Gas | 100% |  |  | Gas | 15 | 90 |  | 275.9 | 40 | 90 |  |  |  | 7.573 | 9.396 |  |  |  | 6.2% | 174 | 5 | 5 | 0.5 | 1 | 63 | 63 | 63 | 12 | 48
ESB | ROI | GU_400182 | AT2 | Aghada CT 2 | Aghada |  | Gas | 100% |  |  | Gas | 15 | 90 |  | 275.9 | 40 | 90 |  |  |  | 7.573 | 9.396 |  |  |  | 6.2% | 174 | 5 | 5 | 0.5 | 1 | 63 | 63 | 63 | 12 | 48
ESB | ROI | GU_400183 | AT4 | Aghada CT 4 | Aghada |  | Gas | 100% |  |  | Gas | 15 | 90 |  | 275.9 | 40 | 90 |  |  |  | 7.573 | 9.396 |  |  |  | 6.2% | 174 | 5 | 5 | 0.5 | 1 | 63 | 63 | 63 | 12 | 48
POWERNI | NI | GU_500140 | B10 | Ballylumford CCGT Unit 10 | Ballylumford Power Station |  | Gas | 100% |  |  | Gas | 63 | 101 | 98.9 | 88.335 | 63 | 101 |  |  |  | 6.003 | 6.003 |  |  |  | 6.2% | 72 | 1.06 | 3.98 | 0.02 | 4 | 135 | 225 | 405 | 8 | 40
POWERNI | NI | GU_500130 | B31 | Ballylumford CCGT Unit 31 | Ballylumford Power Station |  | Gas | 100% |  |  | Gas | 113 | 247 | 244.1 | 351 | 113 | 247 |  |  |  | 5.715 | 5.715 |  |  |  | 6.2% | 72 | 11 | 11 | 0.02 | 4 | 639 | 1134 | 2025 | 8 | 40
POWERNI | NI | GU_500131 | B32 | Ballylumford CCGT Unit 32 | Ballylumford Power Station |  | Gas | 100% |  |  | Gas | 113 | 247 | 244.1 | 351 | 113 | 247 |  |  |  | 5.715 | 5.715 |  |  |  | 6.2% | 72 | 11 | 11 | 0.02 | 4 | 639 | 1134 | 2025 | 8 | 40
EP | NI | GU_500283 | BGT1 | Ballylumford GT1 | Ballylumford Power Station |  | Gasoil | 100% |  |  | Gasoil | 8 | 58 |  | 180 | 8 | 53 | 58 |  |  | 11.05 | 11.05 | 11.05 |  |  | 2% | 24 | 10 | 18 | 0.02 | 0.25 | 8 | 8 | 8
EP | NI | GU_500284 | BGT2 | Ballylumford GT2 | Ballylumford Power Station |  | Gasoil | 100% |  |  | Gasoil | 8 | 58 |  | 180 | 8 | 53 | 58 |  |  | 11.05 | 11.05 | 11.05 |  |  | 2% | 24 | 10 | 18 | 0.02 | 0.25 | 8 | 8 | 8
ESB | NI | GU_500041 | CGT8 | Coolkeeragh OCGT | Coolkeeragh Power Station |  | Gasoil | 100% |  |  | Gasoil | 8 | 53 |  | 180 | 53 |  |  |  |  | 11.05 |  |  |  |  | 2.4% | 176 | 50 | 50 | 0.5 | 0.5 | 8 | 8 | 8 | 0.5 | 0.5
Contour | NI | GU_500904 | Contour AGU | Contour Global Agg Unit | Coolkeeragh Power Station |  | Gas | 100% |  |  | Gas | 6 | 12.084 |  | 15.408 | 9 | 12 |  |  |  | 7.632 | 8.316 |  |  |  | 6.2% | 48 | 4.032 | 4.032 | 0.5 | 0.5 | 0.616 | 0.616 | 0.616
ESB | NI | GU_500040 | CPS CCGT | Coolkeeragh CCGT | Coolkeeragh Power Station |  | Gas | 100% |  |  | Gas | 260 | 404 |  | 633.8 | 260 | 328 | 372 | 404 |  | 4.384 | 5.341 | 5.573 | 5.603 |  | 6.2% | 176 | 15 | 15 | 4 | 4 | 1088 | 1088 | 1088 | 12 | 60
ESB | ROI | GU_400500 | DB1 | Dublin Bay CCGT | Irishtown |  | Gas | 100% |  |  | Gas | 130 | 415 |  | 666 | 130 | 415 |  |  |  | 4.053 | 6.05 |  |  |  | 6.2% | 167 | 10 | 4.48 | 4 | 1 | 2600 | 2600 | 2600 | 12 | 60
Covanta | ROI | GU_402030 | Dublin | Dublin | Irishtown |  | Gasoil | 100% |  |  | Waste | 21.4 | 68.2 | 67.6 | [11 empty] | 6.7% | 36 | 0.9 | 0.9 |  |  | 1279.3 | 1827.5 |  | 24 | >24
BnM | ROI | GU_401860 | ED1 | Edenderry | Cushaling |  | GasOil | 100% |  |  | Peat | 41 | 117.57 |  | 497.6 | 88 | 112 | 118 |  |  | 3.93 | 8.95 | 8.95 |  |  | 7.9% | 72 | 1.76 | 1.76 | 4 | 0.5 | 436 | 1084 | 2308 | 12 | 48
BnM | ROI | GU_401010 | ED3 | Cushaling | Cushaling |  | GasOil | 100% |  |  | Gasoil | 20 | 58 |  | 85 | 58 |  |  |  |  | 9.5 |  |  |  |  | 2.4% | 24 | 5 | 5 |  | 0.5 | 22
BnM | ROI | GU_401011 | ED5 | Cushaling | Cushaling |  | GasOil | 100% |  |  | Gasoil | 20 | 58 |  | 85 | 58 |  |  |  |  | 9.5 |  |  |  |  | 2.4% | 24 | 5 | 5 |  | 0.5 | 22
ESB | ROI | GU_400210 | ER1 | Erne 1 | Cliff |  | Water | 100% |  |  | Water | 0 | 10 | [12 empty] | 4.5% | 86 | 5 | 10
ESB | ROI | GU_400211 | ER2 | Erne 2 | Garvagh |  | Water | 100% |  |  | Water | 0 | 10 | [12 empty] | 4.5% | 86 | 5 | 10
ESB | ROI | GU_400220 | ER3 | Erne 3 | Cathaleen’s Fall |  | Water | 100% |  |  | Water | 0 | 22.5 | [12 empty] | 4.5% | 83 | 10 | 22.5
ESB | ROI | GU_400221 | ER4 | Erne 4 | Cliff |  | Water | 100% |  |  | Water | 0 | 22.5 | [12 empty] | 4.5% | 86 | 10 | 22.5
SSE | ROI | GU_400762 | GI CCGT | Great Island CCGT | Great Island |  | Gas | 100% | 0 | 0 | Gas | 165 | 464 | 458.5 | 605 | 165 | 431 | 464 |  |  | 4.07 | 5.46 | 5.69 |  |  | 5% | 55 | 17.17 | 18.5 | 4 | 4 | 630 | 1700 | 2650 | 12 | 60
Energia Generation | ROI | GU_400540 | HN2 | Huntstown Phase II | Huntstown | 2019-10-01 | Gas | 100% |  |  | Gas | 121 | 404 | 391.88 | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 6.2% | 55 | 20 | 20 | 4 | 4 | 318.454 | 531.129 | 644.171 | 12 | 60
Energia Generation | ROI | GU_400540 | HN2 | Huntstown Phase II | Huntstown | 2021-01-01 | Gas | 100% |  |  | Gas | 121 | 404 | 391.88 | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 6.2% | 55 | 20 | 20 | 4 | 4 | 318.454 | 531.129 | 644.171 | 12 | 60
Energia Generation | ROI | GU_400540 | HN2 | Huntstown Phase II | Huntstown | 2021-10-01 | Gas | 100% |  |  | Gas | 121 | 404 | 391.88 | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 6.2% | 55 | 20 | 20 | 4 | 4 | 318.454 | 531.129 | 644.171 | 12 | 60
Energia Generation | ROI | GU_400540 | HN2 | Huntstown Phase II | Huntstown | 2022-10-01 | Gas | 100% |  |  | Gas | 121 | 404 | 391.88 | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 6.2% | 55 | 20 | 20 | 4 | 4 | 318.454 | 531.129 | 644.171 | 12 | 60
Energia Generation | ROI | GU_400540 | HN2 | Huntstown Phase II | Huntstown | 2023-10-01 | Gas | 100% |  |  | Gas | 121 | 404 | 391.88 | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 6.2% | 55 | 20 | 20 | 4 | 4 | 318.454 | 531.129 | 644.171 | 12 | 60
Energia Generation | ROI | GU_400540 | HN2 | Huntstown Phase II | Huntstown | 2024-05-01 | Gas | 100% |  |  | Gas | 121 | 404 | 391.88 | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 6.2% | 55 | 20 | 20 | 4 | 4 | 318.454 | 531.129 | 644.171 | 12 | 60
Energia Generation | ROI | GU_400480 | HNC | Huntstown | Huntstown | 2019-10-01 | Gas | 100% |  |  | Gas | 120 | 343 | 332.71 | 541.204 | 120 | 171 | 230 | 250 | 352 | 4.528 | 4.53 | 5.237 | 5.247 | 6.039 | 6.2% | 55 | 7 | 7 | 4 | 4 | 834.687 | 2803.196 | 4771.682 | 12 | 60
Energia Generation | ROI | GU_400480 | HNC | Huntstown | Huntstown | 2019-09-01 | Gas | 100% |  |  | Gas | 120 | 343 | 332.71 | 541.204 | 120 | 171 | 230 | 250 | 352 | 4.528 | 4.53 | 5.237 | 5.247 | 6.039 | 6.2% | 55 | 7 | 7 | 4 | 4 | 834.687 | 2803.196 | 4771.682 | 12 | 60
iPower | NI | GU_501130 | iPower AGU | iPower AGU | Aughinish |  | Gasoil | 100% |  |  | Gasoil | 0 | 64 |  | 42.943 |  | 64 |  |  |  | 10.7266 | 10.7266 |  |  |  | 2.4% | 48 | 8 | 8 | 0.5 | 0.5 | 32.1799
Indaver | ROI | GU_401230 | IW1 | Indaver Energy Limited | Aughinish | [5 empty] | Waste | 1 | 17 | [12 empty] | 6.6% | 2.2 | 0.36 | 0.65
EP | NI | GU_500822 | K1 Coal 220 | Kilroot Unit 1 FGD | Kilroot Power Station |  | Oil | 80% | Coal | 20% | Coal | 93 | 255.26 |  | 393.61 | 93 | 174.8 | 255.26 |  |  | 9.4 | 9.4 | 21.5 |  |  | 6% | 72 | 5.79 | 5.79 | 4 | 0.5 | 1984 | 4281 | 5054 | 7.5 | 52.5
EP | NI | GU_500823 | K2 Coal 220 | Kilroot Unit 2 FGD | Kilroot Power Station |  | Oil | 80% | Coal | 20% | Coal | 93 | 257.92 |  | 393.61 | 93 | 174.8 | 257.92 |  |  | 9.4 | 9.4 | 29.49 |  |  | 6% | 72 | 5.79 | 5.79 | 4 | 0.5 | 1984 | 4281 | 5054 | 7.5 | 52.5
EP | NI | GU_500824 | KGT1 | Kilroot GT1 | Kilroot Power Station |  | Gasoil | 100% |  |  | Gasoil | 5 | 29 |  | 103 | 5 | 23.6 | 29.2 |  |  | 11.05 | 11.05 | 11.05 |  |  | 2% | 24 | 6 | 6 | 0.02 | 0.25 | 8 | 8 | 8
EP | NI | GU_500825 | KGT2 | Kilroot GT2 | Kilroot Power Station |  | Gasoil | 100% |  |  | Gasoil | 5 | 29 |  | 103 | 5 | 23.6 | 29.2 |  |  | 11.05 | 11.05 | 11.05 |  |  | 2% | 24 | 6 | 6 | 0.02 | 0.25 | 8 | 8 | 8
EP | NI | GU_500820 | KGT3 | Kilroot GT3 | Kilroot Power Station |  | Gasoil | 100% |  |  | Gasoil | 12.82 | 42 |  | 115.39 | 12.82 | 41.61 |  |  |  | 9.2356 | 9.2356 |  |  |  | 2% | 24 | 10 | 10 | 0.62 | 0.38 | 9.55 | 9.55 | 9.55
EP | NI | GU_500821 | KGT4 | Kilroot GT4 | Kilroot Power Station |  | Gasoil | 100% |  |  | Gasoil | 12.82 | 42 |  | 115.39 | 12.82 | 41.61 |  |  |  | 9.2356 | 9.2356 |  |  |  | 2% | 24 | 10 | 10 | 0.62 | 0.38 | 9.55 | 9.55 | 9.55
ESB | ROI | GU_400280 | LE1 | Lee 1 | Inniscarra |  | Water | 100% |  |  | Water | 0 | 15 | [12 empty] | 4.5% | 123 | 2.4 | 15
ESB | ROI | GU_400281 | LE2 | Lee 2 | Inniscarra |  | Water | 100% |  |  | Water | 0 | 4 | [12 empty] | 4.5% | 123 | 0.6 | 4
ESB | ROI | GU_400290 | LE3 | Lee 3 | Carrigadrohid |  | Water | 100% |  |  | Water | 0 | 8 | [12 empty] | 4.5% | 83 | 1.5 | 8
ESB | ROI | GU_400250 | LI1 | Liffey 1 | Pollaphuca |  | Water | 100% |  |  | Water | 0 | 15 | [12 empty] | 4.5% | 130 | 5 | 10
ESB | ROI | GU_400251 | LI2 | Liffey 2 | Pollaphuca |  | Water | 100% |  |  | Water | 0 | 15 | [12 empty] | 4.5% | 130 | 5 | 10
ESB | ROI | GU_400252 | LI4 | Liffey 4 | Pollaphuca |  | Water | 100% |  |  | Water | 0 | 4 | [12 empty] | 4.5% | 90 | 2 | 2
ESB | ROI | GU_400260 | LI5 | Liffey 5 | Pollaphuca |  | Water | 100% |  |  | Water | 0 | 4 | [12 empty] | 4.5% | 130 | 0.03 | 0.1
ESB | ROI | GU_400270 | MP1 | Moneypoint 1 | Moneypoint |  | Coal | 68% | Oil | 32% | Coal | 75 | 285 |  | 215.4 | 75 | 140 | 195 | 280 | 285 | 8.906 | 8.99 | 9.192 | 9.242 | 13.696 | 9.1% | 284 | 1.63 | 1.33 | 6 | 5 | 4360 | 4360 | 4360 | 12 | 60
ESB | ROI | GU_400271 | MP2 | Moneypoint 2 | Moneypoint |  | Coal | 68% | Oil | 32% | Coal | 99 | 285 |  | 215.4 | 99 | 140 | 195 | 280 | 285 | 8.937 | 8.966 | 9.192 | 9.242 | 13.696 | 9.1% | 283 | 1.63 | 1.33 | 6 | 5 | 4360 | 4360 | 4360 | 12 | 60
ESB | ROI | GU_400272 | MP3 | Moneypoint 3 | Moneypoint |  | Coal | 68% | Oil | 32% | Coal | 75 | 285 |  | 215.4 | 75 | 140 | 195 | 280 | 285 | 8.906 | 8.99 | 9.192 | 9.242 | 13.696 | 9.1% | 284 | 1.63 | 1.33 | 6 | 5 | 4360 | 4360 | 4360 | 12 | 60
ESB | ROI | GU_403680 | n_CDF |  | North Wall | 2022-10-01 | Gas | 100% |  |  | Gas | 27.5 | 70 |  |  | 27.5 | 70 |  |  |  | 8.78 | 8.78 |  |  |  | 6.2% |  | 0 |  |  |  | 50 | 50 | 50
ESB | ROI | GU_403650 | n_NW4 | northwall 4 GT | North Wall | 2022-10-01 | Gas | 100% |  |  | Gas | 42 | 118 |  | 300 | 42 | 118 |  |  |  | 9.47 | 9.47 |  |  |  | 6.2% |  | 30 | 30 | 1 | 1 | 100 | 100 | 100 | 4 | 12
ESB | ROI | GU_400311 | n_NW5 | North Wall 5 refurb | North Wall | 2022-10-01 | Gas | 100% |  |  | Gas | 42 | 118 |  | 300 | 42 | 118 |  |  |  | 9.47 | 9.47 |  |  |  | 6.2% |  | 30 | 30 | 1 | 1 | 100 | 100 | 100 | 4 | 12
ESB | ROI | GU_403620 | n_PB |  | North Wall | 2022-10-01 | Gas | 100% |  |  | Gas | 27.5 | 70 |  |  | 27.5 | 70 |  |  |  | 8.78 | 8.78 |  |  |  | 6.2% |  | 0 |  |  |  | 50 | 50 | 50
ESB | ROI | GU_403610 | n_RNS |  | North Wall | 2022-10-01 | Gas | 100% |  |  | Gas | 27.5 | 70 |  |  | 27.5 | 70 |  |  |  | 8.78 | 8.78 |  |  |  | 6.2% |  | 0 |  |  |  | 50 | 50 | 50
ESB | ROI | GU_400311 | NW5 | North Wall 5 | North Wall |  | Gas | 100% |  |  | Gas | 19 | 109 |  | 318.8 | 50 | 109 |  |  |  | 8.627 | 9.272 |  |  |  | 6.2% | 328 | 8 | 5.82 | 1 | 1 | 50 | 50 | 50 | 12 | 48
ESB | ROI | GU_400324 | PBA | Poolbeg C_A | Poolbeg |  | Gas | 100% |  |  | Gas | 120 | 255 |  | 352.9 | 145 | 240 | 255 |  |  | 5.435 | 6.057 | 7.007 |  |  | 6.2% | 154 | 5 | 5 | 1 | 1 | 750 | 750 | 750 | 12 | 48
ESB | ROI | GU_400325 | PBB | Poolbeg C_B | Poolbeg |  | Gas | 100% |  |  | Gas | 120 | 255 |  | 352.9 | 145 | 240 | 255 |  |  | 5.435 | 6.057 | 7.007 |  |  | 6.2% | 154 | 5 | 5 | 1 | 1 | 750 | 750 | 750 | 12 | 48
Aughinish | ROI | GU_400120 | SK3 | Sealrock 3 (Aughinish CHP) | Aughinish |  | Gas | 100% |  |  | Gas | 40 | 83 |  | 100 | 40 | 83 |  |  |  | 5 | 5 |  |  |  | 1% | 44 | 6 | 6 | 4 | 4 | 800 | 1000 | 1200 | 12 | 48
Aughinish | ROI | GU_400121 | SK4 | Sealrock 4 (Aughinish CHP) | Aughinish |  | Gas | 100% |  |  | Gas | 40 | 83 |  | 100 | 40 | 83 |  |  |  | 5 | 5 |  |  |  | 1% | 44 | 6 | 6 | 4 | 4 | 800 | 1000 | 1200 | 12 | 48
SSE | ROI | GU_400750 | TB1 | Tarbert Unit 1 | Tarbert |  | Oil | 61% | Gasoil | 39% | Oil | 18 | 54 | 0 | 44.66 | 20 | 46 | 54 |  |  | 11.63 | 11.63 | 11.75 |  |  | 2% | 50 | 1 | 1 | 2 | 2 | 217.5 | 449 | 562 | 12 | 48
SSE | ROI | GU_400751 | TB2 | Tarbert Unit 2 | Tarbert |  | Oil | 61% | Gasoil | 39% | Oil | 18 | 54 | 0 | 44.66 | 20 | 46 | 54 |  |  | 11.63 | 11.63 | 11.75 |  |  | 2% | 50 | 1 | 1 | 2 | 2 | 217.5 | 449 | 562 | 12 | 48
SSE | ROI | GU_400752 | TB3 | Tarbert Unit 3 | Tarbert |  | Oil | 70% | Gasoil | 30% | Oil | 34.85 | 243 | 0 | 247.61 | 34.85 | 100 | 180 | 240 |  | 8.0698 | 8.0698 | 9.063 | 9.153 |  | 2% | 50 | 2 | 2.2 | 4 | 4 | 1072 | 1934 | 3180 | 14 | 106
SSE | ROI | GU_400753 | TB4 | Tarbert Unit 4 | Tarbert |  | Oil | 70% | Gasoil | 30% | Oil | 34.85 | 243 | 0 | 247.61 | 34.85 | 100 | 180 | 240 |  | 8.4 | 8.4 | 9.428 | 9.64 |  | 2% | 50 | 2 | 2.2 | 4 | 4 | 1072 | 1934 | 3180 | 14 | 106
ESB | ROI | GU_400360 | TH1 | Turlough Hill 1 | Turlough Hill |  | Water | 100% |  |  | Water | 0 | 73 | [12 empty] | 6% | 123 | 0
ESB | ROI | GU_400361 | TH2 | Turlough Hill 2 | Turlough Hill |  | Water | 100% |  |  | Water | 0 | 73 | [12 empty] | 6% | 123 | 0
ESB | ROI | GU_400362 | TH3 | Turlough Hill 3 | Turlough Hill |  | Water | 100% |  |  | Water | 0 | 73 | [12 empty] | 6% | 123 | 0
ESB | ROI | GU_400363 | TH4 | Turlough Hill 4 | Turlough Hill |  | Water | 100% |  |  | Water | 0 | 73 | [12 empty] | 6% | 123 | 0
SSE | ROI | GU_400780 | TP1 | Tawnaghmore 1 | Tawnaghmore |  | Gasoil | 100% | 0 | 0 | Gasoil | 5 | 52 | 0 | 86.62 | 12 | 52 |  |  |  | 9.5867 | 9.5867 |  |  |  | 2.4% | 123 | 10 | 10 | 0 | 0.75 | 24 | 0 | 0 | 0 | 0
SSE | ROI | GU_400781 | TP3 | Tawnaghmore 3 | Tawnaghmore |  | Gasoil | 100% | 0 | 0 | Gasoil | 5 | 52 | 0 | 86.62 | 12 | 52 |  |  |  | 9.5867 | 9.5867 |  |  |  | 2.4% | 50 | 10 | 10 | 0 | 0.75 | 24 | 0 | 0 | 0 | 0
Tynagh Energy Limited | ROI | GU_400530 | TY | Tynagh | Tynagh |  | Gas | 100% |  |  | Gas | 194 | 404 |  | 594 | 194 | 200 | 280 | 320 | 404 | 4.7297 | 5.0739 | 5.1158 | 5.5018 | 5.9738 | 6.2% | 64.5 | 15 | 12.5 | 4 | 4 | 1200 | 2000 | 3000 | 12 | 48
BGE | ROI | GU_400930 | WG | Whitegate | Whitegate |  | Gas | 100% |  |  | Gas | 160 | 445 | 432 | 666.7 | 185 | 399 | 460 |  |  | 3.91 | 5.265 | 5.265 |  |  | 6.2% | 32.1 | 20.6 | 26.8 | 4 | 4 | 222.6 | 329.9 | 437.1 | 12 | 60
|  |  |  | Carrickaduff | Croaghnagawna |  | Wind |  |  |  | Wind | 0 | 66 | [14 empty] | 0
|  |  |  | Carrickalangan | Croaghnagawna |  | Wind |  |  |  | Wind | 0 | 72 | [14 empty] | 0
|  |  |  | Firlough WF | Firlough |  | Wind |  |  |  | Wind | 0 | 48.3 | [14 empty] | 0
|  |  |  | Garvagh - Glebe (1a) | Garvagh |  | Wind |  |  |  | Wind | 0 | 26 | [14 empty] | 0
|  |  |  | Garvagh - Tullynahaw (1c) | Garvagh |  | Wind |  |  |  | Wind | 0 | 22 | [14 empty] | 0
|  |  |  | Golagh (1) | Golagh |  | Wind |  |  |  | Wind | 0 | 15 | [14 empty] | 0
|  |  |  | Lenalea | Lenalea |  | Wind |  |  |  | Wind | 0 | 30.5 | [14 empty] | 0
|  |  |  | Kingsmountain (1) | Cunghill |  | Wind |  |  |  | Wind | 0 | 24 | [14 empty] | 0
|  |  |  | Kingsmountain (2) | Cunghill |  | Wind |  |  |  | Wind | 0 | 11 | [14 empty] | 0
|  |  |  | Meentycat (1) | Meentycat |  | Wind |  |  |  | Wind | 0 | 71 | [14 empty] | 0
|  |  |  | Meentycat (2) | Meentycat |  | Wind |  |  |  | Wind | 0 | 14 | [14 empty] | 0
|  |  |  | Mountain Lodge (1) | Ratrussan |  | Wind |  |  |  | Wind | 0 | 31 | [14 empty] | 0
|  |  |  | Mullygaffy | Tievebrack |  | Wind |  |  |  | Wind | 0 | 29.9 | [14 empty] | 0
|  |  |  | Mulreavy (1) | Mulreavy |  | Wind |  |  |  | Wind | 0 | 82 | [14 empty] | 0
|  |  |  | Mulreavy Ext | Mulreavy |  | Wind |  |  |  | Wind | 0 | 13 | [14 empty] | 0
|  |  |  | Oriel (1) | Oriel |  | Wind |  |  |  | Wind | 0 | 210 | [14 empty] | 0
|  |  |  | Ratrussan (1a) | Ratrussan |  | Wind |  |  |  | Wind | 0 | 48 | [14 empty] | 0
|  |  |  | Gallanstown Solar | Gallanstown |  | Solar |  |  |  | Solar | 0 | 119 | [14 empty] | 0
|  |  |  | Harristown Solar PV | Harristown |  | Solar |  |  |  | Solar | 0 | 42 | [14 empty] | 0
|  |  |  | Blundlestown | Blundelstown |  | Solar |  |  |  | Solar | 0 | 60 | [14 empty] | 0
|  |  |  | Cloncreen Wind farm | Cloncreen |  | Wind |  |  |  | Wind | 0 | 75 | [14 empty] | 0
|  |  |  | Gaskinstown | Deenes |  | Solar |  |  |  | Solar | 0 | 85 | [14 empty] | 0
|  |  |  | Gillinstown Solar | Garballagh |  | Solar |  |  |  | Solar | 0 | 95 | [14 empty] | 0
|  |  |  | Timahoe North | Timahoe |  | Solar |  |  |  | Solar | 0 | 70 | [14 empty] | 0
|  |  |  | Blackwater Bog Solar 1 | Derrylahan |  | Solar |  |  |  | Solar | 0 | 65 | [14 empty] | 0
|  |  |  | Clonfad Solar | Clonfad |  | Solar |  |  |  | Solar | 0 | 100 | [14 empty] | 0
|  |  |  | Cloghan Wind Farm | Derrycarney |  | Wind |  |  |  | Wind | 0 | 34 | [14 empty] | 0
|  |  |  | Loughteague | Coolnabacky |  | Solar |  |  |  | Solar | 0 | 55 | [14 empty] | 0
|  |  |  | Mountlucas (1) | Mountlucas |  | Wind |  |  |  | Wind | 0 | 79 | [14 empty] | 0
|  |  |  | Boolinrudda | Ennis |  | Wind |  |  |  | Wind | 0 | 46 | [14 empty] | 0
|  |  |  | Booltiagh (1) | Booltiagh |  | Wind |  |  |  | Wind | 0 | 19 | [14 empty] | 0
|  |  |  | Booltiagh (2) | Booltiagh |  | Wind |  |  |  | Wind | 0 | 12 | [14 empty] | 0
|  |  |  | Dromada (1) | Dromada |  | Wind |  |  |  | Wind | 0 | 29 | [14 empty] | 0
|  |  |  | Kill Hill (1) | Kill Hill |  | Wind |  |  |  | Wind | 0 | 36 | [14 empty] | 0
|  |  |  | Knockalassa | Ennis |  | Wind |  |  |  | Wind | 0 | 27 | [14 empty] | 0
|  |  |  | Lisheen (1) | Lisheen |  | Wind |  |  |  | Wind | 0 | 36 | [14 empty] | 0
|  |  |  | Lisheen (1a) | Lisheen |  | Wind |  |  |  | Wind | 0 | 19 | [14 empty] | 0
|  |  |  | Lisheen 3 | Lisheen |  | Wind |  |  |  | Wind | 0 | 29 | [14 empty] | 0
|  |  |  | Moneypoint WF | Moneypoint |  | Wind |  |  |  | Wind | 0 | 18 | [14 empty] | 0
|  |  |  | Ballywater | Ballywater |  | Wind |  |  |  | Wind | 0 | 42 | [14 empty] | 0
|  |  |  | Castledockrell | Castledockrill |  | Wind |  |  |  | Wind | 0 | 42 | [14 empty] | 0
|  |  |  | Knocknamona | Dungarvan |  | Wind |  |  |  | Wind | 0 | 34 | [14 empty] | 0
|  |  |  | Woodhouse | Woodhouse |  | Wind |  |  |  | Wind | 0 | 20 | [14 empty] | 0
|  |  |  | Athea | Athea |  | Wind |  |  |  | Wind | 0 | 34 | [14 empty] | 0
|  |  |  | Ballinknockane Solar Farm | Ballinknockane |  | Solar |  |  |  | Solar | 0 | 50 | [14 empty] | 0
|  |  |  | Banemore Solar Farm | Clahane |  | Solar |  |  |  | Solar | 0 | 34 | [14 empty] | 0
|  |  |  | Boggeragh (1) | Boggeragh |  | Wind |  |  |  | Wind | 0 | 57 | [14 empty] | 0
|  |  |  | Boggeragh (2) | Boggeragh |  | Wind |  |  |  | Wind | 0 | 48 | [14 empty] | 0
|  |  |  | Clahane (1) | Clahane |  | Wind |  |  |  | Wind | 0 | 38 | [14 empty] | 0
|  |  |  | Clahane (2) | Clahane |  | Wind |  |  |  | Wind | 0 | 14 | [14 empty] | 0
|  |  |  | Cloghboola | Cloghboola |  | Wind |  |  |  | Wind | 0 | 46 | [14 empty] | 0
|  |  |  | Coomacheo (1) | Garrow |  | Wind |  |  |  | Wind | 0 | 41 | [14 empty] | 0
|  |  |  | Coomacheo (2) | Garrow |  | Wind |  |  |  | Wind | 0 | 18 | [14 empty] | 0
|  |  |  | Coomagearlahy (1) | Coomagearlahy |  | Wind |  |  |  | Wind | 0 | 43 | [14 empty] | 0
|  |  |  | Coomagearlahy (2) | Coomagearlahy |  | Wind |  |  |  | Wind | 0 | 9 | [14 empty] | 0
|  |  |  | Coomagearlahy (3) | Coomagearlahy |  | Wind |  |  |  | Wind | 0 | 30 | [14 empty] | 0
|  |  |  | Cordal | Cordal |  | Wind |  |  |  | Wind | 0 | 90 | [14 empty] | 0
|  |  |  | Drombeg Solar Park | Drombeg |  | Solar |  |  |  | Solar | 0 | 50 | [14 empty] | 0
|  |  |  | Glanlee (1) | Glanlee |  | Wind |  |  |  | Wind | 0 | 30 | [14 empty] | 0
|  |  |  | Glen Solar | Glen |  | Solar |  |  |  | Solar | 0 | 40 | [14 empty] | 0
|  |  |  | Grousemount | Coomataggart |  | Wind |  |  |  | Wind | 0 | 114 | [14 empty] | 0
|  |  |  | Kelwin | Kilpaddoge |  | Wind |  |  |  | Wind | 0 | 27 | [14 empty] | 0
|  |  |  | Killavoy | Boggeragh |  | Wind |  |  |  | Wind | 0 | 18 | [14 empty] | 0
|  |  |  | Knockacummer (1) | Knockacummer |  | Wind |  |  |  | Wind | 0 | 105 | [14 empty] | 0
|  |  |  | Tobertoreen | Athea |  | Wind |  |  |  | Wind | 0 | 34 | [14 empty] | 0
|  |  |  | Tullabeg Solar Park | Tullabeg |  | Solar |  |  |  | Solar | 0 | 50 | [14 empty] | 0
|  |  |  | Buffy | Buffy |  | Wind |  |  |  | Wind | 0 | 91 | [14 empty] | 0
|  |  |  | Carrigdangan | Carrigdangan |  | Wind |  |  |  | Wind | 0 | 68 | [14 empty] | 0
|  |  |  | Derrybrien (1) | Derrybrien |  | Wind |  |  |  | Wind | 0 | 60 | [14 empty] | 0
|  |  |  | Knockalough | Knockalough |  | Wind |  |  |  | Wind | 0 | 34 | [14 empty] | 0
|  |  |  | Killala (1) | Tawnaghmore |  | Wind |  |  |  | Wind | 0 | 19 | [14 empty] | 0
|  |  |  | Killala (2) | Tawnaghmore |  | Wind |  |  |  | Wind | 0 | 11 | [14 empty] | 0
|  |  |  | Oweninney (1) | Bellacorick |  | Wind |  |  |  | Wind | 0 | 89 | [14 empty] | 0
|  |  |  | Oweninney (2) | Bellacorick |  | Wind |  |  |  | Wind | 0 | 83 | [14 empty] | 0
|  |  |  | Oweninney (3) | Bellacorick |  | Wind |  |  |  | Wind | 0 | 50 | [14 empty] | 0
|  |  |  | Seecon (1) | Knockranny |  | Wind |  |  |  | Wind | 0 | 108 | [14 empty] | 0
|  |  |  | Shannonbridge ESS | Shannonbridge |  | Wind |  |  |  | Wind | 0 | 63 | [14 empty] | 0
|  |  |  | Shantallow Solar | Shantallow |  | Solar |  |  |  | Solar | 0 | 35 | [14 empty] | 0
|  |  |  | Sheskin | Bellacorick |  | Wind |  |  |  | Wind | 0 | 33 | [14 empty] | 0
|  |  |  | Sliabh Bawn (1) | Sliabh Bawn |  | Wind |  |  |  | Wind | 0 | 58 | [14 empty] | 0
|  |  |  | Ugool | Uggool |  | Wind |  |  |  | Wind | 0 | 66 | [14 empty] | 0

## Sheet1
Table D-1 MEC of Existing and Committed Transmission-Connected Generation
[6 empty] | Connection Year (if future) | Maximum Export Capacity (MW) | Capacity |  |  | Heat Rate Curve | [10 empty] | Forced Outages |  | TOD |  |  |  | Starts
Area | Generation Station | Unit ID | Connected At |  | Fuel Type |  |  | Min Stable Capacity (MW) | Max Capacity (MW) | Summer Rating--Where Different (MW) | No Load Heat Requirement (GJ/hr) | Capacity point 1 (MW) | Capacity point 2 (MW) | Capacity point 3 (MW) | Capacity point 4 (MW) | Capacity point 5 (MW) | Heat Rate Inc 1 (GJ/MWh) | Heat Rate Inc 2 (GJ/MWh) | Heat Rate Inc 3 (GJ/MWh) | Heat Rate Inc 4 (GJ/MWh) | Heat Rate Inc 5 (GJ/MWh) | Forced Outage Rate,% | Mean Time to Repair, hrs | Ramp Rate Up, MW/min | Ramp Rate Down, MW/min | Min Up Time (hrs) | Min Down Time (hrs) | Start up Energy (GJ) Hot | Start up Energy (GJ) Warm | Start up Energy (GJ) Cold | Hot to Warm boundary, hrs | Warm to Cold boundary, hrs
| Carrickaduff |  | Croaghnagawna | 110 kV | Wind | 2023 | 66
| Carrickalangan |  | Croaghnagawna | 110 kV | Wind | 2023 | 72
| Erne Cathleens Fall Hydro (3) |  | Cathaleen’s Fall | 110 kV | Hydro |  | 22
| Erne Cathleens Fall Hydro (4) | ER3 | Cathaleen’s Fall | 110 kV | Hydro |  | 23
| Erne Cliff Hydro (1) | ER4 | Cliff | 110 kV | Hydro |  | 10
| Erne Cliff Hydro (2) | ER1 | Cliff | 110 kV | Hydro |  | 10
| Firlough WF |  | Firlough | 110 kV | Wind |  | 48.3
| Garvagh - Glebe (1a) | ER2 | Garvagh | 110 kV | Wind |  | 26
| Garvagh - Tullynahaw (1c) |  | Garvagh | 110 kV | Wind |  | 22
| Golagh (1) |  | Golagh | 110 kV | Wind |  | 15
| Lenalea |  | Lenalea | 110 kV | Wind | 2025 | 30.5
Border | Kingsmountain (1) |  | Cunghill | 110 kV | Wind |  | 24
| Kingsmountain (2) |  | Cunghill | 110 kV | Wind |  | 11
| Lisdrumdoagh Energy Storage Facility |  | Lisdrum | 110 kV | Battery |  | 60
| Meentycat (1) |  | Meentycat | 110 kV | Wind |  | 71
| Meentycat (2) |  | Meentycat | 110 kV | Wind |  | 14
| Mountain Lodge (1) |  | Ratrussan | 110 kV | Wind |  | 31
| Mullygaffy |  | Tievebrack | 110 kV | Wind |  | 29.9
| Mulreavy (1) |  | Mulreavy | 110 kV | wind |  | 82
| Mulreavy Ext |  | Mulreavy | 110 kV | Wind |  | 13
| Oriel (1) |  | Oriel | 0.69 kV | Wind | 2022 | 210
| Ratrussan (1a) |  | Ratrussan | 110 kV | Wind |  | 48
| Corduff |  | Corduff | 220 kV | Battery | 2022 | 70
| Dublin Bay Power | DB1 | Irishtown | 220 kV | Gas/Oil |  | 415
| Gallanstown Solar |  | Gallanstown | 110 kV | Solar | 2023 | 119
| Harristown Solar PV |  | Harristown | 110 kV | Solar | 2023 | 42
| Huntstown (1) | HNC | Huntstown | 220 kV | Gas/Oil |  | 236
Dublin | Huntstown (1) | HNC | Huntstown | 220 kV | Gas/Oil |  | 123
| Huntstown (2) | HN2 | Huntstown | 220 kV | Gas |  | 412
| Shellybanks Com- bined Cycle | PBC | Shellybanks | 220 kV | Gas/Oil |  | 150
| Shellybanks Com- bined Cycle | PBC | Shellybanks | 220 kV | Gas/Oil |  | 150
| Shellybanks Com- bined Cycle | PBC | Shellybanks | 220 kV | Gas/Oil |  | 173
| Blundlestown |  | Blundelstown | 110 kV | Solar |  | 60
| Cloncreen Wind farm |  | Cloncreen | 110 kV | Wind | 2025 | 75
| Gaskinstown |  | Deenes | 110 kV | Solar | 2022 | 85
| Gillinstown Solar |  | Garballagh | 110 kV | Solar | 2023 | 95
| Gorman BES |  | Gorman | 110 kV | Battery | 2023 | 50
| Liffey Hydro (1) | LI1 | Pollaphuca | 110 kV | Hydro |  | 15
| Liffey Hydro (2) | LI2 | Pollaphuca | 110 kV | Hydro |  | 15
Mid-East | Liffey Hydro (4) | LI4 | Pollaphuca | 110 kV | Hydro |  | 4
| Porterstown BES |  | Kilteel | 110 kV | Battery |  | 30
| Timahoe North |  | Timahoe | 110 kV | Solar | 2023 | 70
| Turlough Hill (1) | TH1 | Turlough Hill | 220 kV | Pumped Storage |  | 73
| Turlough Hill (2) | TH2 | Turlough Hill | 220 kV | Pumped Storage |  | 73
| Turlough Hill (3) | TH3 | Turlough Hill | 220 kV | Pumped Storage |  | 73
| Turlough Hill (4) | TH4 | Turlough Hill | 220 kV | Pumped Storage |  | 73
| Blackwater Bog Solar 1 |  | Derrylahan | 110 kV | solar | 2023 | 65
| Clonfad Solar |  | Clonfad | 110 kV | solar | 2022 | 100
| Cloghan Wind Farm |  | Derrycarney | 110 kV | Wind | 2024 | 34
| Edenderry Peaking | ED3 | Cushaling | 110 kV | Conventional |  | 117
Midlands | Edenderry Power | ED1 | Cushaling | 110 kV | Peat |  | 134
| Lanesboro (2) |  | Lanesboro | 110 kV | Peat |  | 40
| Lanesboro (3) |  | Lanesboro | 110 kV | Peat |  | 45
| Loughteague |  | Coolnabacky | 110 kV | solar | 2025 | 55
| Lumcloon Batt |  | Derrycarney | 110 kV | Battery |  | 100
| Mountlucas (1) |  | Mountlucas | 110 kV | Wind |  | 79
| Rhode PCP (1) | RP1 | Derryiron | 110 kV | Distillate |  | 52
| Rhode PCP (2) | RP2 | Derryiron | 110 kV | Distillate |  | 52
| Alumina CHP (1) | SK3 | Aughinish | 110 kV | Gas |  | 86
| Alumina CHP (1) | SK4 | Aughinish | 110 kV | Gas |  | 86
| Ardnacrusha Hydro (1) | AA1 | Ardnacrusha | 110 kV | Hydro |  | 21
| Ardnacrusha Hydro (2) | AA2 | Ardnacrusha | 110 kV | Hydro |  | 22
| Ardnacrusha Hydro (3) | AA3 | Ardnacrusha | 110 kV | Hydro |  | 19
| Ardnacrusha Hydro (4) | AA4 | Ardnacrusha | 110 kV | Hydro |  | 24
| Boolinrudda |  | Ennis | 110 kV | Wind |  | 46
| Booltiagh (1) |  | Booltiagh | 110 kV | Wind |  | 19
Mid-West | Booltiagh (2) |  | Booltiagh | 110 kV | Wind |  | 12
| Dromada (1) |  | Dromada | 110 kV | Wind |  | 29
| Kill Hill (1) |  | Kill Hill | 110 kV | Wind |  | 36
| Knockalassa |  | Ennis | 110 kV | Wind |  | 27
| Lisheen (1) |  | Lisheen | 110 kV | Wind |  | 36
| Lisheen (1a) |  | Lisheen | 110 kV | Wind |  | 19
| Lisheen 3 |  | Lisheen | 110 kV | Wind | 2022 | 29
| Moneypoint (1) | MP1 | Moneypoint | 380 kV | Coal |  | 302
| Moneypoint (2) | MP2 | Moneypoint | 380 kV | Coal |  | 305
| Moneypoint (3) | MP3 | Moneypoint | 380 kV | Coal |  | 302
| Moneypoint WF |  | Moneypoint | 380 kV | Wind |  | 18
| Ballylumford | B31 | Ballylumford | 275 kV | Gas |  | 250
| Ballylumford | B32 | Ballylumford | 276 kV | Gas |  | 250
| Ballylumford 10 | B10 | Ballylumford Power Station | 110 kV | Gas |  | 100
| Ballylumford GT1 | BGT1 | Ballylumford Power Station | 110 kV | Gas |  | 58
| Ballylumford GT2 | BGT2 | Ballylumford Power Station | 110 kV | Gas |  | 58
| Castlereagh BES |  | Castlereagh | 110 kV | Battery | 2023 | 50
| Coolkeeragh GT | CPS CCGT | Coolkeeragh Power Station | 275 kV | Gas |  | 404
| Coolkeeragh GT8 | CGT8 | Coolkeeragh Power Station | 110 kV | Oil |  | 53
Northern Ireland | Coolkeeragh ST | C30 GS | Coolkeeragh Power Station | 110 kV | Gas |  | 170
| Kilroot GT3 | KGT3 | Kilroot Power Station | 275 kV | Distillate |  | 42
| Kilroot GT4 | KGT4 | Kilroot Power Station | 275 kV | Distillate |  | 42
| KELLS_BES |  | Kells | 110 kV | Battery | 2023 | 50
| Kilroot OCGT6 |  | Kilroot Power Station | 275 kV | Gas | 2023 | 406
| Kilroot OCGT7 |  | Kilroot Power Station | 275 kV | Gas | 2023 | 302
| Kilroot ST1 | K1 | Kilroot Power Station | 275 kV | Coal/Oil |  | 195
| Kilroot ST2 | K2 | Kilroot Power Station | 275 kV | Coal/Oil |  | 195
| Tamnamore BES |  | TAMNAMORE | 110 kV | Battery |  | 50
| Tandragee BES |  | Tandragee | 110 kV | Battery |  | 50
| Ballywater |  | Ballywater | 110 kV | Wind |  | 42
| Castledockrell |  | Castledockrill | 110 kV | Wind |  | 42
| Great Island CCGT | GI4 | Great Island | 220 kV | Conven- tional |  | 439
South-East | Knocknamona |  | Dungarvan | 110 kV | Wind |  | 34
| Rathnaskilloge |  | Rathnaskillo | 110 kV | solar | 2023 | 95
| Rosspile Solar Farm |  | Rosspile | 110 kV | Solar | 2023 | 95
| Woodhouse |  | Woodhouse | 110 kV | Wind |  | 20
| Aghada CCGT | ADC | Aghada | 220 kV | Gas |  | 442 | 130 | 440 |  | 589.4 | 130 | 200 | 320 | 380 | 440 | 3.177 | 5.297 | 5.393 | 5.757 | 5.814 | 6.2% | 192 | 8.83 | 12.38 | 4 | 4 | 1200 | 1200 | 1200 | 12 | 60
| Aghada | AT1 | Aghada | 220 kV | Gas |  | 90 | 15 | 90 |  | 275.9 | 40 | 90 |  |  |  | 7.573 | 9.396 |  |  |  | 6.2% | 174 | 5 | 5 | 0.5 | 1 | 63 | 63 | 63 | 12 | 48
| Aghada | AT2 | Aghada | 220 kV | Gas |  | 90 | 15 | 90 |  | 275.9 | 40 | 90 |  |  |  | 7.573 | 9.396 |  |  |  | 6.2% | 174 | 5 | 5 | 0.5 | 1 | 63 | 63 | 63 | 12 | 48
| Aghada | AT4 | Aghada | 220 kV | Gas |  | 90 | 15 | 90 |  | 275.9 | 40 | 90 |  |  |  | 7.573 | 9.396 |  |  |  | 6.2% | 174 | 5 | 5 | 0.5 | 1 | 63 | 63 | 63 | 12 | 48
| Aghada BESS 1 |  | Aghada | 220 kV | storage |  | 19
| Aghada BESS 2 |  | Aghada | 220 kV | Storage |  | 159
| Athea |  | Athea | 110 kV | Wind |  | 34
| Ballinknockane Solar Farm |  | Ballinknockane | 110 kV | Solar | 2023 | 50
| Banemore Solar Farm |  | Clahane | 110 kV | Solar |  | 34
| Boggeragh (1) |  | Boggeragh | 110 kV | Wind |  | 57
| Boggeragh (2) |  | Boggeragh | 110 kV | Wind |  | 48
| Clahane (1) |  | Clahane | 110 kV | Wind |  | 38
| Clahane (2) |  | Clahane | 110 kV | Wind |  | 14
| Cloghboola |  | Cloghboola | 110 kV | Wind |  | 46
| Coomacheo (1) |  | Garrow | 110 kV | Wind |  | 41
| Coomacheo (2) |  | Garrow | 110 kV | Wind |  | 18
South-West | Coomagearlahy (1) |  | Coomagearlahy | 110 kV | Wind |  | 43
| Coomagearlahy (2) |  | Coomagearlahy | 110 kV | Wind |  | 9
| Coomagearlahy (3) |  | Coomagearlahy | 110 kV | Wind |  | 30
| Cordal |  | Cordal | 110 kV | Wind |  | 90
| Drombeg Solar Park |  | Drombeg | 110 kV | Solar | 2022 | 50
| Glanlee (1) |  | Glanlee | 110 kV | Wind |  | 30
| Glen Solar |  | Glen | 110 kV | solar | 2024 | 40
| Grousemount |  | Coomataggart | 110 kV | Wind |  | 114
| Kelwin |  | Kilpaddoge | 220 kV | Wind |  | 27
| Kelwin Battery |  | Kilpaddoge | 220 kV | storage | 2024 | 42
| Killavoy |  | Boggeragh | 110 kV | Wind |  | 18
| Knockacummer (1) |  | Knockacummer | 110 kV | Wind |  | 105
| Lee Carrigadrohid Hydro (1) |  | Carrigadrohid | 110 kV | Hydro |  | 8
| Lee Inniscarra Hydro (1) |  | Inniscarra | 110 kV | Hydro |  | 19
| Tarbert (1) | TB1 | Tarbert | 110 kV | HFO |  | 57
| Tarbert (2) | TB2 | Tarbert | 110 kV | HFO |  | 57
| Tarbert (3) | TB3 | Tarbert | 220 kV | HFO |  | 256
| Tarbert (4) | TB4 | Tarbert | 220 kV | HFO |  | 258
| Tobertoreen |  | Athea | 110 kV | Wind |  | 34
| Tullabeg Solar Park |  | Tullabeg | 110 kV | Solar | 2023 | 50
| Whitegen CCGT | WG | Glanagow | 220 kV | Gas |  | 449
| Buffy |  | Buffy | 110 kV | Wind |  | 91
| Carrigdangan |  | Carrigdangan | 110 kV | Wind | 2023 | 68
| Derrybrien (1) |  | Derrybrien | 110 kV | Wind |  | 60
| Knockalough |  | Knockalough | 110 kV | Wind |  | 34
| Killala (1) |  | Tawnaghmore | 110 kV | Wind |  | 19
| Killala (2) |  | Tawnaghmore | 110 kV | Wind | 2023 | 11
| Oweninney (1) |  | Bellacorick | 110 kV | Wind |  | 89
| Oweninney (2) |  | Bellacorick | 110 kV | Wind |  | 83
| Oweninney (3) |  | Bellacorick | 110 kV | Wind | 2023 | 50
West | Seecon (1) |  | Knockranny | 110 kV | Wind |  | 108
| Shannonbridge ESS |  | Shannonbridge | 220 kV | Battery |  | 100
| Shannonbridge ESS |  | Shannonbridge | 220 kV | Wind |  | 63
| Shantallow Solar |  | Shantallow | 110 kV | Solar | 2023 | 35
| Sheskin |  | Bellacorick | 110 kV | Wind | 2023 | 33
| Sliabh Bawn (1) |  | Sliabh Bawn | 110 kV | Wind |  | 58
| Tawnaghmore Peak- ing Plant | TP1 | Tawnaghmore | 110 kV | distillate |  | 52
| Tawnaghmore Peak- ing Plant | TP2 | Tawnaghmore | 110 kV | distillate |  | 52
| Tynagh | TY1 | Tynagh | 220 kV | Gas |  | 268
| Tynagh | TY2 | Tynagh | 220 kV | Gas |  | 142
| Ugool |  | Uggool | 110 kV | Wind |  | 66